## Jan 2021
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment

## Feb 2021
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
22/2/2021 | MBE 5 TR | HT | Temperature was OK on chiller display but CMS Sensor was giving HT Alarm | Changed the Sub-Zero Display |  |  | 0 | 5 | Amit
23/2/2021 | 1.1&1.2 Lab | HT | Temperature was OK on chiller display but CMS Sensor was giving HT Alarm | Changed the Temperature Sensor |  |  | 0 | 5 | Amit

## March 2021
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment

## April 2021
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2021-04-04 | Micro 1 10 TR | LL | Low Level - false alarm | Cleaned sensor |  |  | 0 | 5 | Irwin
2021-08-04 | MBE 10 TR | HT | High Temperature | Changed ICMS Temp Sensor |  |  | 0 | 5 | Irwin
2021-08-04 | Micro 1 10 TR | LL | Low Level - false alarm | Cleaned sensor |  |  | 0 | 5 | Irwin
2021-09-04 | Micro 1 10 TR | LL | Low Level - false alarm | Cleaned sensor |  |  | 0 | 5 | Rajendra
17/4/2021 | MBE 10 TR | CP | OL of Comp 2 showing on display | reset contactor |  |  | 0 | 5 | Irwin
| MBE 10 TR | CP | OL of Comp 2 showing on display | reset contactor and increased OL Setting little bit |  |  | 0 | 5 | Irwin
30/4/2021 | M1 YR 5 TR | HT | High Temperature | Leak found in chiller R-22 Circuit. Attended the leak and topped up the R-22 Gas 55 PSI |  | 18 |  | 5 | Sanjay, Amit, Irwin

## May 2021
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
17/5/2021 | M1 YR 5 TR | HT | High Temperature | Reset contactor & increased OL Setting inside Chiller Control Panel |  |  | 0 | 5 | Sandeep, Irwin
20/5/2021 | MBE 10 TR | LL | Low Level | Tank water level was OK cleaned the level sensor |  |  | 0 | 5 | Irwin
22/5/2021 | Dynacool | LL | Low Level | Tank water level was OK cleaned the level sensor |  |  | 0 | 5 | Irwin

## June 2021
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2021-09-06 | Dynacool 5TR | LL | Low Level | Cleaned the sensor cable |  |  | 0 | 5 | Irwin

## July 2021
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment

## August 2021
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment

## September 2021
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment

## October 2021
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment

## November 2021
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment

## December 2021
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment

## March 2020
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment

## February 2020
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment

## January 2020
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment

## December 2019
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2019-09-12 | Dynacool | HT | High Temp | Swapped to New Chiller |  |  | 0 | 5 | Sanjay Salve | In Night Shift

## November 2019
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2019-01-11 | MBE 10 TR | LL | Low Level | Cleaned sensor cable and later on attached new level sensor to the cable | 0 |  |  | 5 | Amit, Irwin
| Dynacool | LP | Low Pressure |  | 0 |  |  |  |  | Momentary alarm then stopped by itself. Not came after that again.
2019-04-11 | Nano 10 TR | HT | High Temp | On Chiller Display the reading is OK i.e. 16 Deg C so cleaned temp sensor but still alarm came so put off ICMS. Need to change the temp sensor. | 0 |  |  | 5 | Sanjay, Irwin
2019-07-11 | Nano 10 TR | HT | High Temp | Changed the sensor wire and sub zero controller inside Nano Lab | 0 |  |  | 5 | Amit, Ajay B

## October 2019
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2019-08-10 | Micro 1 10 TR | LL | Low Level | ICMS put off later on water level top up done |  |  | 0 |  | Raju K
2019-12-10 | Micro 1 10 TR | LL | Low Level | ICMS put off later on water level top up done |  |  | 0 |  | Raju K
27/10/2019 | Dynacool | HT | High Temp | Swapped to standby/new chiller |  |  | 0 |  | Sanjay

## September 2019
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2019-02-09 | Micro 1 10 TR | LL | Sensor dirty | Clean sensor Properly |  |  | 0 | 10 | Amit
2019-03-09 | MBE | LL | Sensor dirty | Clean sensor Properly |  |  | 0 | 10 | Sanjay/Amit
2019-04-09 | Nano 10 TR | LL | Low Level | ICMS put off later on water level top up done |  |  | 0 | 5 | Irwin
14/9/2019 | Micro 1 10 TR | LL | Low Level | ICMS put off later on water level top up done |  |  | 0 | 5 | Sanjay

## August 2019
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2019-01-08 | Micro 1 10 TR | LL | Low Level | 2 Bucket RO Water top up done |  |  | 0 | 5 | Raju K
19/8/2019 | Micro 1 10 TR | CP | LP in Comp 2 | Found leak in 2 places and did brazing and connection near compressor discharge side service valve tightened |  |  | 0 | 5 | Amit, Irwin
30/8/2019 | Dynacool | CP | LP [Low Pressure] in Old Chiller Compressor | Swapped to standby system after finding leak near HP Cut Out and Filter Dryer |  |  | 0 |  | Dynacool PPMS System is OFF

## July 2019
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2019-03-07 | Nano 10 TR | CP | PP | Reset the connection to the display |  |  | 0 | 5 | Amit
2019-04-07 | Dynacool | CP | PP | Reset the connection to the display |  |  | 0 | 5 | Irwin
2019-11-07 | Nano 10 TR | LL | Low Level | 4 Buckets RO Water topped up |  |  | 0 | 5 | Raju K, Hitesh B

## June 2019
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2019-03-06 | 1.1 chiller | HT | PP | cleaned sensor |  |  |  | 5 | Raju | HT alarm come again and again so finally changed the sensor now no issue.
2019-08-06 | M1YR 5 TR chiller | PP | Low water level | Top up RO water |  |  |  | 10 | Rajendra, Sanjay, Irwin
19/6/2019 | 1.1&1.2 Lab | CP | Probe Problem | Changed the temp sensor |  |  | 0 | 5 | Amit
2019-08-06 | M1 YR 5 TR | PP | Probe Problem | Put off compressor, changed sensor and topped up RO Water in chiller tank |  |  | 0 | 5 | Rajendra, Sanjay, Irwin
24/6/2019 | MBE 10 TR | CP | Low Temp | Changed the temp sensor |  |  | 0 | 5 | Amit
5

## May 2019
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2019-05-05 | Nano 10 TR | LL | Low Level | RO Water top up |  | 0 |  | 5 | Raju K
2019-08-05 | Nano 10 TR | LL | Low Level | RO Water top up |  | 0 |  | 5 | Raju K
2019-12-05 | Nano 10 TR | CP | PP | Reset the connection to display |  | 0 |  | 5 | Raju K
19/5/2019 | Dynacool Chiller | HT | High Temperature | Reset HP Cut Out and Contactor |  | 0 |  | 5 | Raju K, Sandeep M
26/5/2019 | MBE 10 TR | CP | PP | Reset the connection to display |  | 0 |  | 5 | Amit
28/5/2019 | Micro 1 Lab 10 TR | CP | PP | Reset the connection to display |  | 0 |  | 5 | Amit
| Nano 10 TR | LL | Low Level | RO Water top up |  | 0 |  | 5 | Raju K

## April 2019
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2019-08-04 | 1.1&1.2 Lab | LL | Low Level due to water leak from new water filter installed for AJA System | Replaced the housing and found old housing had no gasket which was the cause for leak. Did water top up in chiller immediately and LL Alarm stopped. |  |  | 0 | 5 | Hitesh B, Amit, Irwin
25/4/2019 | Dynacool Chiller - Char 2 Lab | CP | PP | Swap the sensor cable |  |  | 0 | 5 | Amit, Sanjay
27/4/2019 | Micro 1 10 TR | CP | HP | Reset HP Cut Out |  |  | 0 | 5 | Sanjay Salve

## March 2019
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2019-01-03 | Nano 10 TR | LL | Low Level | 4 Buckets RO Water topped up |  |  | 0 | 5 | Hitesh B
2019-06-03 | Dynacool | CP | PP | Cleaned temp sensor and put back into chiller tank |  |  | 0 | 5 | Amit, Sanjay
14/3/2019 | Nano 10 TR | LL | Low Level | 3 Buckets RO Water topped up |  |  | 0 | 5 | Hitesh B
16/3/2019 | 1.1&1.2 Lab | LL | Low Level | Water Top Up Done |  |  | 0 | 5 | Raju K

## February 2019
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2019-11-02 | MBE 10 TR | LL | Low Level | Found the water level was 13 - 14 coils down so did water top up |  |  | 0 | 5 | Irwin
2019-12-02 | Nano 10 TR | LL | Low Level | Cleaned level sensor and readjusted level in water tank |  |  | 0 | 5 | Irwin
14/2/2019 | MBE 10 TR | HT | High Temp but on display the temp was showing 19.5 deg C. Still MBE Students said the turbo water temp was high. Did blower cleaning of condenser coil and gas pressure readings checked. Found OK. After blower cleaning the issue got resolved. |  |  |  | 0 | 5 | Raju K, Irwin
16/2/2019 | Nano 10 TR | LL | 2 Buckets RO Water Top Up |  |  |  | 0 | 5
17/2/2019 | Dynacool | LL | 3 Buckets RO Water Top Up |  |  |  | 0 | 5 | Raju K
18/2/2019 | MBE 10 TR | 3 Times CP & On Display PP | First Time cleaned temp sensor and issue got resolved |  |  |  | 0 | 5
|  |  | Second Time changed both temp sensors |  |  |  | 0 | 5
|  |  | Third Time installed a temp sensor directly to the chiller control pcb to keep cooling while another spare cable identified and then the issue got resolved |  |  |  | 0 | 5 | Rajendra S, Hitesh B, Irwin
19/2/2019 | Nano 10 TR | LL | Low Level | 2 Buckets RO Water top up done |  |  | 0 | 5 | Irwin
22/2/2019 | MBE 5 TR | LL | Low Level | RO Water top up and issue attended and resolved |  |  | 0 | 0 | Facility Team: Sandeep M, Rajendra S, Sanjay, Irwin
23/2/2019 | MBE 5 TR | LL | Low Level | Found water level only 4 - 5 coils down. Did top up after taking water from NCPRE Fab Lab. |  |  | 0 | 5 | Irwin
23/2/2019 | Dynacool | HT | High Temp | Did blower cleaning |  |  | 0 | 5 | Hitesh B, Irwin

## January 2019
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2019-01-01 | Nano 10 TR | LL | Low Level | 2 Bucket RO Water filled | 0 | 0 | 0 | 5 | Sanjay
2019-02-01 | Dynacool | LL | Low Level | 2 Bucket RO Water filled | 0 | 0 | 0 | 5 | Raju K
| M1 10 TR | CP | Comp 2 LP | R-22 gas top up done | 0 | 0 | 0 | 5 | Amit, Hitesh B, Irwin
2019-11-01 | 1.1 | LL | Low Level |  | 0 | 0 | 0 | 5 | Raju K | Alarm came for 1 second then stopped by itself
2019-12-01 | Dynacool | LL | Low Level | 1 Bucket RO Water topped up in chiller tank | 0 | 0 | 0 | 5 | Irwin | Still LL alarm came 1 sec again at 8:43 am

## December 2018
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2018-01-12 | Nano chiller | LL | Water level low | top up 4 bucket RO water |  |  | 10 | 5 | Raju
2018-02-12 | Nano chiller | PP | Probe fail | changed water temp sensor |  |  | 30 | 5 | Amit, Irwin, Raju
2018-03-12 | MBE chiller | CP | comp 1 LP trip | top up 20% RO water |  |  |  | 1 hour | Amit, hitesh, Irwin
13/12/2018 | Nano chiller | LL | Water level low | top up 2 bucket Ro water |  |  |  | 5 | Raju
25/12/2018 | MBE 10 TR | CP | Low Temp Issue | Sensor changed |  |  |  | 10 | Amit, Sanjay | 2 times the same issue came in 1 day
28/12/2018 | MBE 10 TR | CP | Low Temp Issue | Sensor changed |  |  |  | 5 | Amit
30/12/2018 | M1 10 TR | CP
| M1 10 TR | LL | Low Level | 1 Bucket RO water filled |  |  |  | 5 | Raju, Sanjay
| Nano 10 TR | LL | Low Level | 4 Buckets RO water filled |  |  |  | 5 | Sanjay
31/12/2018 | Nano 10 TR | PP on display | PP | Redid connection of cable to display |  |  |  | 5 | Irwin

## November 2018
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2018-02-11 | nano | LL | Low level due to tool flushing | top up 2 bucket RO water |  |  | 0 | 5 | Irwin
13/11/2018 | M1 Lab chiller | LL | Low level | top up 2 bucket RO water |  |  | 0 | 5 | Raju
13/11/2018 | dynacool chiller | LL | Low level sensor rusted | cleaned sensor and put back in tank |  |  | 0 | 5 | AMIT
14/11/2018 | dynacool chiller | cp | cms water temp sensor issue | laying new sensor wire and changed sensor. |  | 2 |  | 1 days | AMIT,IRWIN
25/11/2018 | dynacool chiller | cp | unforeseen issue, controller mulfunction | need seperate panel for new compresor. |  |  | 0 | 0 | Sandeep, Irwin, Amit
29/11/2018 | MBE chiller | CP | water level low | top up 25% ro water |  |  | 0 | 1 Days | Irwin, Amit
30/11/2018 | Nano chiller | PP alarm came in CMS panel which is mounted in Nano lab | Sensor faulty | need to replace sensor |  |  | 0 | 30 minutes | Amit, Raju, Irwin

## October 2018
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2018-11-10 | 1.1 lab | LL | low level | top up 2 bucket water |  |  | 0 | 5 | raju
2018-12-10 | dynacool chiller | HT/CP | both compressor tripping on HT | reset hpcut out and increase setting |  |  | 0 | 5 | Amit
19/10/18 | nano chiller | LL | low level | top up 2 bucket water |  |  | 0 | 5 | sanjay
20/10/2018 | dynacoolchiller | HT | controller not working | replaced chiller controller and display

## September 2018
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2018-01-09 | Nano 10 TR | HT | High Temperature but on display the temperature is OK | Put off CMS and later on redid the connection of temperature sensor cable in nano lab service corridor |  |  | 0 | 5 | Irwin
17/9/2018 | 1.1 Lab | LP | Low Pressure alarm came in CMS/ICMS | Readjusted the Pressure Switch @ chiller manifold |  |  | 0 | 5 | Hitesh B
18/9/2018 | Nano 10 TR | LL | Low Level | 2 buckets RO Water topped up in chiller water tank |  |  | 0 | 5 | Amit, Hitesh B
28/9/2018 | Dynacool | CP/HT | Compressor HP Alarm on display | Swapped to new chiller unit |  |  | 0 | 5 | Amit
30/9/2018 | Dynacool | CP/HT | Compressor HP Alarm on display | Cleaned old condenser coil by blower but still HP came, reset HP LP Cut Out 2 times but no success so swapped to New Chiller. Increased HP Setting to 350 psi in view of changing climate. |  |  | 0 | 5 | Amit, Irwin

## August 2018
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2018-05-08 | Dynacool Chiller | HT | High Temp due to PP on display | Reconnected display cable |  |  | 0 | 5 | Hitesh B
2018-10-08 | MBE 10 TR Chiller | LL | Low Level | Cleaned level sensor and put back in the tank |  |  | 0 | 5 | Raju K
16/8/2018 | Dynacool Chiller | HT | High Temperature | Cleaned the temperature sensor and re-immersed in chiller water tank |  |  | 0 | 5 | Hitesh B
20/8/2018 | Nano 10 TR Chiller | LL | Low Level | 2 Buckets RO Water topped up in chiller water tank |  |  | 0 | 5 | Raju K
30/8/2018 | Dynacool Chiller | LL | Low Level | 3 Buckets RO Water topped up in chiller water tank |  |  | 0 | 5 | Hitesh B, Amit Das
31/8/2018 | Nano 10 TR Chiller | HT | High Temperature | Sensor cleaned and put back in chiller tank |  |  | 0 | 5 | Raju K | Later on same morning sensor changed. HB/SS/AIR
|  | LP | Low Pressure alarm came for 1 second and then stopped. No trip of any sputters of Nano Lab. |  |  |  | 0 | 5 | Irwin
|  | LL | Low Level | 1 Bucket RO Water topped up |  |  | 0 | 5 | Hitesh B

## July 2018
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2018-03-07 | 1.1 & 1.2 Lab Chiller | LP | Low Pressure | Readjusted the bypass valve at chiller manifold |  |  | 0 | 5 | Sanjay, Amit
17/7/2018 | Dynacool Chiller | LL | Low Level | 2 buckets RO Water topped up |  |  | 0 | 5 | Raju K | In night shift @ 1:00 am the alarm came
17/07/2018 | NCPRE Chiller | LL | Low Level | Changed leval sensor |  |  | 0 | 5 | Amit, Shindey
30/7/2018 | Nano 10 TR Chiller | LL | Low Level | 2 buckets RO Water topped up |  |  | 0 | 5 | Hitesh B

## June 2018
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2018-05-06 | Nano 10 TR | LL | Low Level | 2 bucket RO Water top up done |  |  | 0 |  | Amit, Irwin
15/6/2018 | 1.1 Chiller | LP & HT | Low Pressure | Reset pressure switch @ manifold |  |  | 0 |  | Facility Team
|  |  | High Temp | Reset HP LP cut out of Cooling Unit [Comp] 2 |  |  | 0 |  | Facility Team
18/06/2018 | Nano 10 TR | LL | Low Level | 2 bucket RO water top up |  |  | 0 |  | Raju
19/6/2018 | Nano 10 TR | ll | Low Level | 2 bucket RO water top up |  |  | 0 |  | Raju

## May 2018
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
18/5/2018 | NCPRE | CP | None but checking chiller suction pressure after PM completed | [5 empty] | Amit Das. P Shinde
21/5/2018 | Nano 10 TR | LL | Low Level | 2 bucket RO Water topped up |  |  |  |  | Irwin
25/5/2018 | Dynacool Chiller | HT | [6 empty] | Sanjay | Put off the chiller for further checking
28/5/2018 | Dynacool Chiller | CP | LP | [5 empty] | Sanjay | Put off the chiller for further checking

## April 2018
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2018-02-04 | MBE 10 tr chiller | HT | Comp 1 HT trip | Clean condenser coil with air blower and reset lp/hp cut out | 0 | 0 | 30 | 5 | Hitesh
2018-04-04 | Nano chiller | LL | water level low | Top up ro water | 0 | 0 | 15 | 5 | Raju
25/4/2018 | Dynacool Chiller | CP | PP on display. | Reset the display connection | 0 | 0 | 0 | 5 | Sanjay
28/4/2018 | Nano chiller | LL | water level low | 1.5 bucket RO Water top up done | 0 | 0 | 0 | 5 | Sanjay

## March 2018
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2018-04-03 | Dynacool Chiller | HT | High Temp as per CMS | Checked Dynacool Chiller display but found compressor tripped on temperature and temp was 17 deg C | 0 | 0 | 0 | 5 | Irwin
2018-07-03 | 1.1 Chiller | LL | Low Level | Redid the connection | 0 | 0 | 0 | 5 | Rajendra S, Irwin
| Nano 10 TR | LL | Low Level | It came due to ALD System water flushing being done by EMT. At 3:30 PM 2 buckets RO Water filled and CMS put on. | 0 | 0 | 0 | 5 | Irwin
2018-08-03 | 1.1 Chiller | LL | Low Level | Redid the connection | 0 | 0 | 0 | 5 | Irwin
2018-09-03 | 1.1 Chiller | LL | Low Level | Redid the connection but alarm coming repeatedly so put off CMS mcb | 0 | 0 | 0 | 5 | Irwin
2018-11-03 | M1 10 TR | LL | Low Level | 3 Buckets RO Water filled & sensor cleaned | 0 | 0 | 0 | 5 | Hitesh B
|  | CP | Comp 1 HP Trip | Reset HP LP cut out | 0 | 0 | 0 | 5 | Hitesh B, Irwin
2018-12-03 | M1 10 TR | CP | Comp 1 HP trip | Reser LP/HP cut out and change hp setting 330 Psig before setting is 300 | 0 | 0 | 10 | 5 | Amit, Irwin
14/03/2018 | M1 10 TR | LL | water leval low | top up 2 bucket ro water | 0 | 0 | 10 | 5 | sanjay
15/03/2018 | M1 10 TR | LL | Sensor wire rusted | Clean wire and connect sensor | 0 |  | 30 | 5 | Amen, Amit
15/03/2018 | Nano | LP | chiller pump fluctuate | Swap to stand by pump | 0 | 0 | 10 | 0 | Amen
16/03/2018 | Nano | LL | water leval low | top up 2 bucket ro water | 0 | 0 | 20 | 5 | Amit,Raju
20/03/2018 | Nano | LL | water leval low | top up 2 bucket ro water | 0 | 0 | 20 | 5 | Raju
22/03/2018 | MBE | CP | PP alarm on main panel | Change temp sensor | 0 | 0 | 20 | 5 | Amen, Amit
25/03/2018 | 1.1 Lab | CP | Comp 1 HP trip | Change setting and reset HP/LP cutout | 0 | 0 | 30 | 5 | Amit
25/03/2018 | 1.1 Lab | CP | Comp 2 HP trip | Change setting and reset HP/LP cutout | 0 | 0 | 30 | 5 | Amit
25/03/2018 | MBE | CP | Comp 2 HP trip | Change setting and reset HP/LP cutout | 0 | 0 | 30 | 5 | Amit
26/03/2018 | Nano | LL | water leval low | top up 2 bucket ro water | 0 | 0 | 10 | 5 | Raju
26/03/2018 | M1 10 TR | CP | Comp-2 HP trip | Reset HP LP cut out | 0 | 0 | 10 | 5 | Amit

## February 2018
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2018-01-02 | M1 10 TR | LL | Low Level | 3 Bucket RO Water topped up & sensor cable joint cleaned and put back into water tank | 0 | 0 | 0 | 5 | Hitesh B, Irwin
15/2/2018 | Dynacool Chiller | HT | High Temperature
22/2/2018 | Dynacool Chiller | HT, CP | PP Alarm came in CMS/ICMS
25/2/2018 | M1 10 TR | HP | High Pressure | Reset HP LP Cut Out and did blower cleaning of condenser coil |  |  |  |  | Hitesh B, Irwin
27/2/2018 | M1 10 TR | HP | High Pressure | Reset HP LP Cut Out |  |  |  |  | Hitesh B, Irwin
28/2/2018 | M1 10 TR | HP | High Pressure | Reset HP LP Cut Out |  |  |  |  | Hitesh B, Irwin
| MBE 10 TR | LL | Low Level | 2 Buckets RO Water topped up |  |  |  |  | Hitesh B
| MBE 5TR | LL | Low Level | Sensor cleaned and put back in tank |  |  |  |  | Hitesh B
| 1.1 Lab | LP | Low Pressure | Pressure switch adjustment done |  |  |  |  | Irwin

## January 2018
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2018-08-01 | Nano 10 TR | LL | Low Level | RO Water top up | 0 | 0 | 0 | 5 | Raju K
| MBE 10 TR | HT | High Temperature | Found secondary sensor came out of tank to kept inside tank again | 0 | 0 | 0 | 5 | Amit
2018-09-01 | Nano 10 TR | LL | Low Level | 1 Bucket RO Water top up done | 0 | 0 | 0 | 5 | Raju K
2018-10-01 | Nano 10 TR | LL | Low Level | 2 Buckets RO Water top up done | 0 | 0 | 0 | 5 | Hitesh B
2018-11-01 | MBE 10 TR | CP | CP | Went off by itself | 0 | 0 | 0 | 5 | Raju K
2018-12-01 | MBE 10 TR | LL | Low Level | 2 Buckets RO Water top up done | 0 | 0 | 0 | 5 | Sanjay, Irwin
14/1/2018 | 1.1 Chiller | LL | Low Level | 4 Buckets RO Water top up done | 0 | 0 | 0 | 5 | Raju K
17/1/2018 | 1.1 Chiller | LL | Low Level | Sensor cleaned and put back in water tank | 0 | 0 | 0 | 5 | Sanjay
19/1/2018 | MBE 5TR | LL | Low Level |  | 0 | 0 | 0 | 5 | Sanjay
22/1/2018 | Nano 10 TR | LL | Low Level | 2 Bucket RO Water Top Up | 0 | 0 | 0 | 5 | Rajendra S, P Shinde

## December 2017
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
14/12/2017 | Nano 10 TR | LL | Low Level | 2 buckets RO Water top up done | 0 | 0 | 0 | 5 | Amit
18/12/2017 | Micro 1 10 TR Chiller | LL Alarm came in CMS/ICMS | Low Level | 2 Buckets RO Water added and sensor cleaned |  |  |  |  | Hitesh B
| MBE 10 TR Chiller | LL Alarm came in CMS/ICMS | Low Level | 2 Buckets RO Water added and sensor cleaned |  |  |  |  | Hitesh B
21/12/2017 | M1 10 TR Chiller | LL Alarm came in CMS/ICMS | Low Level | Sensor cleaned |  |  |  |  | Raju K
25/12/2017 | Dynacool Chiller | HT | High Temp | HP LP Cut Out reset |  |  |  |  | Sanjay
|  | HT | High Temp | Cleaned sensor and put back in water tank |  |  |  |  | Rajendra

## November 2017
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2017-02-11 | MBE | LL | Low Level | Water top up done and sensor cleaned | 0 | 0 | 0 | 5 | Amit, Rajendra, Hitesh B, Irwin
2017-03-11 | Dynacool | HT | High Temp | Cleaned the ssnsor and put back in the water tank | 0 | 0 | 0 | 5 | Sanjay
2017-06-11 | Dynacool | HT | High Temp | Cleaned the ssnsor and put back in the water tank | 0 | 0 | 0 | 5 | Sanjay
2017-09-11 | Nano 10 TR | LL | Low Level - due to Raith System water line flushing going on | 6 Buckets RO Water topped up in morning by Amit and 2 more buckets RO Water topped up in evening by Hitesh B & Irwin | 0 | 0 | 0 | 10 | Hitesh B, Irwin, Amit
2017-11-11 | Dynacool Chiller | HT | High Temp | Cleaned the sensor and put back in the water tank | 0 | 0 | 0 | 10 | Sanjay
| 1.1 Chiller | HT | High Temp | Put off CMS/ICMS till sensor replacement done on 13/11/2017 evening 5:00 PM | 0 | 0 | 0 | 10 | Raju K, Amit, Irwin
15/11/2017 | Nano 10 TR | LL | Low Level | 2 Bucket RO Water top up done | 0 | 0 | 0 | 5 | Irwin
19/11/2017 | Dynacool Chiller | HT | High Temp | Cleaned the sensor and put back in the water tank | 0 | 0 | 0 | 5 | Sanjay | In second shift
23/11/2017 | MBE 10 TR | LL | Low Level | Cleaned the sensor and put back in the water tank | 0 | 0 | 0 | 5 | Amit, Rajendra, Hitesh B, Irwin
|  | LP | Low Pressure | Swapped to standby pump & adjusted bypass valve @ chiller manifold in MBE Lab Service Corridor | 0 | 0 | 0 | 5 | Amit, Rajendra, Hitesh B, Irwin
26/11/2017 | MBE 10 TR | LL, LP | Low Level, Low Pressure | Pipe burst due to high pressure. Fixed pipe @ joint and filled RO Water again. Found cable of pump solenoid valve flow control unit was cut outside so again re-joined the connection and fixed it properly | 0 | 0 | 0 | 5 | Amit, Raju K, Irwin
| MBE 5 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 5 | Amit, Raju K
| Dynacool Chiller | LL | Low Level | Cleaned the sensor and put back in the water tank | 0 | 0 | 0 | 5 | Amit
28/11/2017 | Nano 10 TR | LL | Low Level | 2 Buckets RO Water top up done | 0 | 0 | 0 | 5 | Sanjay, Amit

## October 2017
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2017-03-10 | Nano Chiller | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 10 | Raju K | In Night Shift
2017-04-10 | Nano Chiller | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 10 | Hitesh B
2017-05-10 | Dynacool Chiller | HT | High Temperature | Reduced gas increased HP Setting | 0 | 0 | 0 | 5 | Amit, Raju K
| Dynacool Chiller | HT | High Temperature | Reduced gas till compressor takes not more than 10.5 Amps | 0 | 0 | 0 | 5 | Amit, Hitesh, Irwin
18/10/2017 | NCPRE Chiller | HT | High Temperature | Came because chiller was put on after PM. Temperature came normal after a short while | 0 | 0 | 0 | 0 | Irwin
19/10/2017 | MBE 10 TR | CP | CP | Came and went within 1 second kept under observation but alarm has not come again | 0 | 0 | 0 | 0 | Irwin
24/10/2017 | Nano Chiller | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 5 | Hitesh B, Irwin
25/10/2017 | MBE 10 TR | HT | High Temperature | Found less water in tank so did top up | 0 | 0 | 0 | 5 | Amit
31/10/2017 | Nano Chiller | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 10 | Amit, Irwin

## September 2017
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2017-09-09 | Dynacool Chiller | LL | Low Level | Water Level top up done and sensor cable cleaned and put in water again | 0 | 0 | 0 | 5 | Irwin | Alarm only came in ICMS, but not in CMS
2017-10-09 | Dynacool Chiller | CP | Low Temperature Issue | Changed the temp sensor | 0 | 0 | 0 | 5 | Amit
2017-10-09 | Micro 1 | CP | HP fault | reset the compressor | 0 | 0 | 0 | 20 | amit
2017-11-09 | Dynacool Chiller | LL | Low Level | Sensor cable cleaned and put back in chiller water tank | 0 | 0 | 0 | 5 | Amit, Sanjay
14/9/2017 | Nano chiller | LL | Low Level | water top up done | 0 | 0 | 0 | 10 | amit
17/9/2017 | Nano chiller | LL | Low Level | 2 buckets RO Water topped up | 0 | 0 | 0 | 10 | Irwin
18/9/2017 | Dynacool Chiller | PP | Probe Problem | Removed connection from display and re-connected | 0 | 0 | 0 | 5 | Irwin | No Alarm came in CMS/ICMS
24/9/2017 | Nano chiller | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 10 | Sanjay
25/9/2017 | Micro 1 | LL | Low Level | Sensor cable cleaned and put back in chiller water tank | 0 | 0 | 0 | 20 | Amit
30/9/2017 | Nano Chiller | LL | Low Level | 1.5 Buckets RO Water top up done | 0 | 0 | 0 | 10 | Hitesh B

## August 2017
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2017-01-08 | Dynacool Chiller | HT | HP Trip & Sensor issue | Reset HP LP cut out of new compressor and changed temp sensor in chiller water tank | 0 | 0 | 0 | 5 | Amit, Ajay B, Irwin
2017-05-08 | 1.1 Lab Chiller | LL | Low Level | Cleaned the sensor cable and put back in the tank | 0 | 0 | 0 | 5 | Irwin
2017-07-08 | 1.1 Lab Chiller | LL | Low Level | Water Top Up Done | 0 | 0 | 0 | 5 | Raju K
2017-10-08 | Nano 10 TR Chiller | LL | Low Level | RO Water top up | 0 | 0 | 0 | 20 | Pawar, Irwin
2017-11-08 | Dynacool Chiller | HT | High Temperature | Swapped to Old Chiller | 0 | 0 | 0 | 5 | Irwin
2017-12-08 | Dynacool Chiller | HT @ 2:05 am | High Temperature | Reset HP LP cut out | 0 | 0 | 0 | 5 | Sanjay Salve
| Dynacool Chiller | HT @ 5:50 am | High Temperature | Reset HP LP cut out | 0 | 0 | 0 | 5 | Sanjay Salve | Dynacool Chiller swapped back to New Chiller @ 3:30 pm on 17/8/2017 after checking suction pressure found normal reading of 60 PSI - Amit & Irwin
| MBE 10 TR Chiller | CP @ 3:30 pm | Controller Problem alarm came and went within less than 1 minute | Kept under observation - but alarm did not come again after that | 0 | 0 | 0 |  | Irwin
19/8/2017 | Nano 10 TR Chiller | LL | Low Level | 2 Buckets RO Water topped up | 0 | 0 | 0 | 5 | Raju K
25/8/2017 | Nano 10 TR Chiller | LL | Low Level | 2 Buckets RO Water topped up | 0 | 0 | 0 | 10 | Irwin
| MBE 10 TR Chiller | CP @ 8:30 pm | Controller Problem alarm came and went within less than 1 minute | Kept under observation - but alarm did not come again after that | 0 | 0 | 0 |  | Irwin
31/8/2017 | MBE 10 TR Chiller | LL & LP | Low Level & Low Pressure | Went service corridor and found Kankat has put on / opened water supply to one more system. Water top up done. | 0 | 0 | 0 | 5 | Sandeep M, Rajendra S, Hitesh B, Irwin

## July 2017
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2017-04-07 | MBE 10 TR | CP | Low Temperature | Changed chiller water temp sensor but no change in status. So quickly put off chiller mcb and put on again and issue got resolved. This happened because chiller controller pcb got hanged. | 0 | 0 | 0 | 10 | Amit, Pawar, Sandeep M
2017-11-07 | NCPRE Chiller | LL | Low Level | Water level topped up after completion of PM | 2 |  |  | 10 | Shinde
15/7/2017 | Dynacool Chiller | HT | High Temperature | Gas Top Up done | 0 |  |  | 10 | Amit, Sanjay
16/7/2017 | Dynacool Chiller | HT | High Temperature | Temp Sensor issue - sensor changed [?] | 0 |  |  | 10 | Ajay B, Sanjay

## June 2017
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
13/6/2017 | AMAT 16 TR | LP | 11 TR Compressor LP alarm came | Found LP setting very low only 10 psi not min 30 psi due to which PHE found gone bad
14/6/2017 | AMAT 16 TR | LL | Low Level | 2 bucket RO water top up done | 0 | 0 | 0 | 10 | Hitesh B, Pawar
15/6/2017 | Dynacool Chiller | HT | High Temperature | Reset the contactor in Dynacool chiller new unit on terrace and adjusted the LP setting to 30 psi from 0 psi | 0 | 0 | 0 | 10 | Amit
27/6/2017 | Dynacool Chiller | HT | High Temperature | Reset the contactor in Dynacool chiller new unit on terrace and adjusted the LP setting to 30 psi from 0 psi | 0 |  |  | 10 | Sanjay
30/6/2017 | AMAT 16 TR | LL | Low Level | Water top up done | 0 |  |  | 10 | Pawar
| AMAT 10 TR | LL | Low Level | Water top up done | 0 |  |  | 10 | Pawar

## May 2017
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2017-01-05 | Dynacool | CP | None found since alarm stopped very soon | Checked to see ice formation @ TXV but found none | 0 | 0 | 0 | 10 | Irwin
2017-03-05 | Dynacool | CP | Low gas pressure of R-407 C | Checked suction pressure with gauge and found low < 40 PSI so gas top up done until suction reached 58 PSI |  |  |  | 10 | Amit, Irwin
2017-09-05 | 1.1 Lab Chiller | LL | Low Level | Cleaned the sensor wire immersed in chiller water tank | 0 | 0 | 0 | 10 | Amit, Irwin
2017-11-05 | AMAT 16 TR Chiller | HT | High Temperature | Found 11 TR Comp mcb tripped so put it on and again put on chiller. | 0 | 5 | 0 | 5 | Hitesh B, Irwin
13/5/2017 | AMAT 16 TR Chiller | HT | High Temperature | Found temperature sensor came out from tank so put it back in tank | 0 | 0 | 0 | 10 | Amit
15/5/2017 | MBE 10 TR Chiller | CP
20/5/2017 | Dynacool | LL | Low Level | Sensor cable in tank has got rusted - cleaned the cable and immersed in tank again | 0 | 0 | 0 | 10 | Amit, Hitesh
22/5/2017 | NANO 10 TR | LL | Low Level | 2 bucket RO water top up done | 0 | 0 | 0 | 20 | Hitesh, Irwin
24/5/2017 | AMAT 16 TR Chiller | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Pawar
27/5/2017 | MBE 10 TR Chiller | LL | Low Level | Sensor cable in tank has got rusted - cleaned the cable and immersed in tank again | 0 | 0 | 0 | 20 | Raju K, Irwin
| AMAT 10 TR Chiller | LP | Low Pressure
29/5/2017 | AMAT 10 TR Chiller | LP | Low Pressure | Chiller was put off |  |  |  |  | Sanjay
31/5/2017 | AMAT 16 TR Chiller | LL | Low Level | 3 buckets RO Water top up done |  |  |  |  | Hitesh B

## April 2017
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2017-01-04 | AMAT 10 TR | HP LP | High Temperature | Switched off the chiller as no process going on and full investigation / checks need to be done |  |  |  |  | Sanjay
2017-05-04 | AMAT 16 TR | LL | Low Level | Water level top up done | 0 | 0 | 0 | 10 | Sanjay, Irwin
2017-06-04 | AMAT 10 TR | LL | Low Level | Tank fully emptied cause of leak not found so chiller put off | [5 empty] | Issue resolved on 7/4/2017. Pipe replacement still pending.
2017-10-04 | NANO 10TR | LL | Low Level | Water level top up done | 0 | 0 | 0 | 10 | Irwin
| 1.1 Lab Chiller | LP | Low Pressure | Reset the pressure switch @ manifold |  |  |  |  | Irwin
17/4/2017 | MBE 10 TR | CP
18/4/2017 | MBE 10 TR | CP |  | Changed TXV inside part and dryer (Blu Berg) since there was block in the line inside TXV |  |  |  |  | Amit, Pawar
| Dynacool Chiller | LL | Low Level | Alarm stopped before got time to respond
19/4/2017 | MBE 10 TR | CP |  | Alarm stopped before got time to respond
20/4/2017 | 1.1 Lab Chiller | CP | Condenser 1 LP | Found both pipes touched near service valve so shut this compressor and did brazing and R-22 top up |  |  |  |  | Amit, Pawar
22/4/2017 | AMAT 16 TR | HT | 11 TR Compressor MCB tripped due to isse in one of the pump | Swapped the pump

## March 2017
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2017-02-03 | Nano 10 TR | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 10 | Amit, Pawar
2017-06-03 | MBE 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Raju K
| AMAT 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Amit, Irwin | Found return pipe from manifold had come out of tank so tank went almost empty. Now that pipe secured by cable ties in both AMAT Chillers.
2017-07-03 | MBE 10 TR | CP | Comp 1 OL | Reset the contactor inside the control panel | 0 | 0 | 0 | 10 | Pawar
2017-10-03 | Nano 10 TR | PP | Probe Problem | Reset the connection | 0 | 0 | 0 | 10 | Pawar
2017-12-03 | Dynacool Chiller | HT | High Temperature | Reset HP LP Cut Out twice as alarm came twice within half an hour and second time blower also used to clean condenser coil. Then alarm stopped. | 0 | 0 | 0 | 5 | Sanjay
17/3/2017 | Nano 10 TR | PP | Probe Problem | Reset the connection to display | 0 | 0 | 0 | 10 | Raju K
19/3/2017 | MBE 10 TR | CP | Comp 1 OL | Reset contactors inside control panel | 0 | 0 | 0 | 10 | Hitesh B | 3 times alarm came within the space of 1 hour
20/3/2017 | 1.1 Chiller | LL | Low Level | Water level top up done | 0 | 0 | 0 | 10 | Raju K
| 1.1 Chiller | LL | Low Level | Cleaned level sensor cable inside chiller water tank | 0 | 0 | 0 | 10 | Amit, Irwin | 3 times alarm came
21/3/2017 | AMAT 16 TR | LL | Low Level | Water level top up done | 0 | 0 | 0 | 10 | Pawar, Irwin
25/3/2017 | Dynacool Chiller | LL | Low Level | Cleaned level sensor cable inside chiller water tank | 0 | 0 | 0 | 10 | Amit, Pawar, Irwin
27/3/2017 | 1.1 Chiller | CP | Comp 1 OL | Shut down the condenser units and did wet cleaning. Before that reset the contactors inside control panel & increased O-L Setting. Showed to Thomas who has confirmed one of the compressor has gone bad. |  |  |  |  | Amit, Hitesh B, Sandeep M, Raju K, Pawar, Irwin | Compressor needs to be replaced
| MBE 10 TR | CP | Comp 1 & 2 HP Trip | Increased HP Setting and reduced R-22 gas in both the compressors |  |  |  |  | Amit, Hitesh B, Irwin | Need to reduce R-22 gas in all chillers compressors
29/3/2017 | 1.1 Chiller | HT | High Temperature | Comp 1 of out door unit checked and found compressor is faulty - shorted with body/earthing |  |  |  |  | Amit, Pawar | Need to replace the faulty compressor

## February 2017
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2017-08-02 | AMAT 10 TR Chiller | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Hitesh B
2017-10-02 | Nano 10 TR | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 10 | Sanjay
15/2/2017 | MBE 10 TR Chiller | CP | Comp 1 HP Trip | Reset the HP LP Cut Out & increased HP Setting. | 0 | 0 | 0 | 10 | Amit, Irwin
16/2/2017 | MBE 10 TR Chiller | CP | Comp 1 HP Trip | Reset the HP LP Cut Out & increased HP Setting. | 0 | 0 | 0 | 10 | Amit, Irwin
17/2/2017 | AMAT 10 TR Chiller | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Ajay, Amit | Alarm came twice once in morning & again in evening
| MBE 10 TR Chiller | CP | Comp 1 HP Trip | Reset the HP LP Cut Out & increased HP Setting. Did condenser coil cleaning by blower. | 0 | 0 | 0 | 10 | Amit, Hitesh B, Sanjay | Need to reduce gas little bit. Thomas also checked along with Amit.
| 1.1 Lab Chiller | HT | High Temp | Sensor in water tank of chiller fully rusted - cleaned and put back and issure was resolved. | 0 | 0 | 0 | 10 | Hitesh B, Sanjay, Irwin | Change the sensor in next PM
23/2/2017 | 1.1 Lab Chiller | CP | Comp 2 OL | Reset the contactor inside control panel | 0 | 0 | 0 | 10
28/2/2017 | MBE 10 TR Chiller | CP | Comp 1 OL | Reset the contactor inside control panel | 0 | 0 | 0 | 10 | Pawar, Irwin

## January 2017
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2017-01-01 | AMAT 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Pawar
2017-02-01 | MBE 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Pawar
2017-03-01 | AMAT 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Sanjay
| Nano 10 TR | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 15 | Sanjay
| AMAT 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Pawar
2017-04-01 | Dynacool | HT | High Temperature | Reset HP LP Cut Out | 0 | 0 | 0 | 10 | Sanjay
| AMAT 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Sanjay
2017-05-01 | AMAT 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Sanjay
2017-06-01 | AMAT 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Raju K
2017-07-01 | AMAT 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Sanjay
| Dynacool | HT | High Temperature | Reset HP LP Cut Out | 0 | 0 | 0 | 10 | Sanjay | cleaned condenser coil with blower
2017-09-01 | Dynacool | HT | High Temperature | Reset HP LP Cut Out | 0 | 0 | 0 | 10 | Pawar
| AMAT 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Hitesh B
| AMAT 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Pawar
2017-10-01 | AMAT 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Irwin
2017-11-01 | AMAT 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Raju K | Cause of water leak has been identified on 13/1/2017 - reason is joint in redundant pipe below AMAT 10 TR manifold
13/1/2017 | Nano 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Sanjay, Irwin
27/1/2017 | Nano 10 TR | LL | Low Level | Water top up done | 0 | 0 | 0 | 10 | Amit

## December 2016
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2016-01-12 | AMAT 16 TR | CP | LP in 11 TR | Found suction line accumulator gone bad after Thomas called | 0 | 0 | 0 |  | Amit, Pawar | New suction line accumulator needs to be fitted in the chiller
2016-01-12 | 1.1 Chiller | LL | Checked and found water level in tank was full so some sensor issue / mal-functioning is going on which needs to be checked |  | 0 | 0 | 0 | 10
2016-01-12 | Nano 10 TR | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 10
2016-02-12 | Nano 10 TR | PP | Probe Problem | RO Water top up done and sensor rubbed by hand then PP issue was resolved | 0 | 0 | 0 | 15 | Pawar | There was some internal miscommunication and CMS was kept off so immediately the alarm was not picked up
| AMAT 10 TR | HT | One compressor has gone bad and its replacement request has been given but still awaiting new replacement | After 15 minutes AMAT process got over then the temperature came down again | 0 | 0 | 0 | 10 | Irwin | Need to get new replacement compressor soon
2016-04-12 | AMAT 10 TR | CP | LP in one compressor | After one second the alarm stopped | 0 | 0 | 0 | 5 | Irwin | Need to get new replacement compressor soon
2016-07-12 | Nano 10 TR | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 15 | Amit, Pawar
2016-12-12 | Nano 10 TR | LL | Low Level | Cryo Compressor pipe came out at chiller manifold | 0 | 0 | 0 | 15 | Raju K | Shut the valve of Cryo Compressor at chiller manifold, RO Water top up done and pipe re-fixed again properly
14/12/2016 | AMAT 10 TR | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 20 | Ajay B, Sanjay
15/12/2016 | AMAT 10 TR | HT | High Temperature | Re-set HP LP Cut Outs in the chiller | 0 | 0 | 0 | 10 | Raju K | Temperature went to 27 deg C on Sub Zero Display of Chiller control panel
16/12/2016 | Nano 10 TR | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 10 | powar
21/12/2016 | Nano 10 TR | PP | Probe Problem | RO Water top up done and sensor rubbed by hand then PP issue was resolved | 0 | 0 | 0 | 15 | Raju K
22/12/2016 | Nano 10 TR | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 15 | Raju K
26/12/2016 | AMAT 10 Tr | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 10 | powar
27/12/2016 | AMAT 10 Tr | LL | Low Level | RO Water top up done | 0 | 0 | 0 | 10 | Raju K
27/12/2016 | Nano 10 TR | PP | Probe Problem | MCB ON/Off | 0 | 0 | 0 | 15 | raju K
31/12/2016 | AMAT 10 TR | LL | Low Level | Water top up done |  |  |  |  | Sanjay

## November 2016
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2016-02-11 | AMAT 10 TR | CP, HT |  |  | 0 | 0 | 0 | 10 | B. S. Pawar, Raju K, Amit, Irwin
2016-04-11 | AMAT 10 TR | LL |  | RO water top up done | 0 | 0 | 0 | 10 | Raju K, Amit
2016-08-11 | AMAT 10 TR | LL |  | RO water top up done | 0 | 0 | 0 | 10 | Hitesh B, Amit
16/11/2016 | AMAT 10 TR | CP |  | Re-set HP LP Cut Out | 0 | 0 | 0 | 10 | Irwin
17/11/2016 | AMAT 10 TR | CP |  | Re-set HP LP Cut Out | 0 | 0 | 0 | 10 | Amit
18/11/2016 | AMAT 10 TR | CP |  | Increased HP LP Setting of Compressor 1 | 0 | 0 | 0 | 10 | Amit
| AMAT 16 TR | CP |  | Found O-L of Cooling Unit 2 (5 TR Compressor) so re-set all the relays and alarm got removed | 0 | 0 | 0 | 10 | Irwin
20/11/2016 | AMAT 10 TR | CP |  | Put CMS off and found 23 deg C on sub zero display of chiller control panel | 0 | 0 | 0 | 10 | Ajay B, Irwin | Repeatedly the same alarm is coming
21/11/2016 | AMAT 10 TR | LL & CP |  | RO water top up done | 0 | 0 | 0 | 10 | Hitesh B
| Nano 10 TR | LL |  | RO water top up done | 0 | 0 | 0 | 10 | Hitesh B | Alarm came after chiller switched on after PM completed
22/11/2016 | Nano 10 TR | HT |  | Found temperature on display OK so put ICMS/CMS mcb off | 0 | 0 | 0 | 10
| AMAT 16 TR | CP |  | Found O-L of Cooling Unit 2 (5 TR Compressor) so re-set all the relays and alarm got removed | 0 | 0 | 0 | 10 | Irwin
23/11/2016 | Nano 10 TR | HT |  | Checked & cleaned the temperature sensor in water tank | 0 | 0 | 0 | 10 | Amit, Hitesh B
|  | LL |  | RO water top up done | 0 | 0 | 0 | 10 | Amit, Ajay
| AMAT 10 TR | CP |  | Changed the TXV and found LP glowing on relay inside control panel. Need gas top up of R-22.\ | 0 | 0 | 0 | 10 | Amit, Ajay, Irwin
|  | LL |  | RO water top up done | 0 | 0 | 0 | 10 | Amit
24/11/2016 | AMAT 10 TR | HT |  | Re-set HP LP Cut Out | 0 | 0 | 0 | 10 | Amit
| 1.1 Chiller | LL |  | Cleaned the sensor in water tank | 0 | 0 | 0 | 10 | Amit | Water level was OK in the tank
25/11/2016 | MBE 10 TR | LL |  | RO water top up done | 0 | 0 | 0 | 10 | Raju K
26//11/2016 | MBE 10 TR | LL |  | Put CMS/ICMS mcb off. Put on again after some time. Then no alarm came. | 0 | 0 | 0 | 10 | B. S. Pawar | Water level was OK in the tank
28/11/2016 | Nano 10 TR | LL |  | RO water top up | 0 | 0 | 0 | 10 | Hitesh B
29/11/2016 | AMAT 16 TR | CP |  | 11 TR Comp issue [LP] | 0 | 0 | 0 | 15 | Amit
30/11/2016 | Dynacool | HT |  | R-407C gas top up done | 0 | 0 | 0 | 120 | Amit, Irwin
| AMAT 16 TR | CP |  | Issue is coming repeatedly despite gas top up done

## October 2016
Date | chiller | Fault | issue | solution | downtime (days) | downtime (hours) | downtime (min) | response time ( min) | staff involved | comment
2016-07-10 | Nano 10 TR | CP Alarm came in ICMS & LP on display for Comp 2 | Put mcb off & next day Dew Point Team came and attended the leak |  |  |  | 0 | 20 | Amit, Sanjay, Irwin
2016-09-10 | Nano 10 TR | LL | Low Level | RO Water top up done |  |  | 0 | 10 | Ajay B
2016-10-10 | Nano 10 TR | LL | Low Level | RO Water top up done |  |  | 0 | 10 | B. S. Pawar, Amit
2016-11-10 | 1.1 Lab Chiller | LL | Found level OK | Issue with sensor |  |  | 0 | 10
13/10/2016 | MBE 10 TR | CP Alarm came in ICMS & HP Trip of Comp 1 on Control Panel Display | Re-set HP LP Cut out & all relays inside the panel |  |  |  | 0 | 5 | B. S. Pawar
| MBE 10 TR | CP Alarm came in ICMS & HP Trip of Comp 1 on Control Panel Display | Re-set HP LP Cut out & all relays inside the panel |  |  |  | 0 | 5 | B. S. Pawar
13/10/2016 | AMAT 10 TR | No Alarm came in CMS / ICMS but water temperature went high to 25 Deg C |  |  | 1 |  |  | 10
14/10/2016 | MBE 10 TR | CP Alarm came in ICMS & HP Trip of Comp 1 on Control Panel Display | Re-set HP LP Cut Out & increased the setting @ cut out a little bit |  |  |  | 0 | 10 | Amit, irwin
14/10/2016 | 1.1 Lab Chiller | LL |  |  |  |  | 0
17/10/2016 | 1.1 Lab Chiller | LL |  |  |  |  | 0 |  | B. S. Pawar
|  | LP |  |  |  |  | 0
20/10/2016 | Nano 10 TR | LL |  |  |  |  | 0 |  | Sanjay
21/10/2016 | Nano 10 TR | LL |  |  |  |  | 0 |  | B. S. Pawar
22/10/2016 | Nano 10 TR | LL | RO Water Top Up Done |  |  |  | 0 |  | B. S. Pawar
| Nano 10 TR | LL | RO Water Top Up Done |  |  |  | 0 |  | Ajay B
24/10/2016 | Nano 10 TR | LL | RO Water Top Up Done |  |  |  | 0 |  | Irwin
| Nano 10 TR | LL | RO Water Top Up Done |  |  |  | 0 | 5 | Sanjay, Raju, Amit, Irwin | Found small/minor leak at the bottom of circulation pump that is in use. Tightened the jubilee clip around pump by allen key. Need to swap to stand by pump and attend issue in this pump.
25/10/2016 | Nano 10 TR | LL | RO Water Top Up Done |  |  |  | 0 | 10 | Amit, Sanjay
| Nano 10 TR | LL | RO Water Top Up Done |  |  |  | 0 | 10 | Ajay B
26/10/2016 | Nano 10 TR | LL | RO Water Top Up Done |  |  |  | 0 | 15 | Hitesh B
| Nano 10 TR | LL | RO Water Top Up Done |  |  |  | 0 | 15 | Ajay B
30/10/2016 | Amat 10 TR | LL | RO Water Top Up Done |  |  |  | 0 | 10 | Raju K
31/10/2016 | Nano 10 TR | LL | RO Water Top Up Done |  |  |  | 0 | 10 | Raju K

## September 2016
Date | chiller | Fault | issue | solution | downtime (min) | response time ( min) | staff involved | comment
2016-02-09 | Nano 10 TR | LL | Low Level | RO Water top up | 0 | 20 | Raju K | This alarm came because of leakage found in the chiller manifold which was attended on the spot
2016-04-09 | Amat 16 TR | CP | LP on display | Found small leakage in suction line of 11 TR Compressor | 0 |  | Raju K, Amit, Irwin | Staff involved to completey resolve this issue on 6/9/2016 were: Amit, Sanjay, Pawar, Raju K
2016-07-09 | Nano 10 TR | LL | Low Level | Due to pipe coming loose at Orion Sputter manifold inside the lab so re-connected the pipe. | 0 |  | Ajay B, Rajendra S | This manifold needs to be shifted outside of Nano Lab
2016-09-09 | Dynacool Chiller | CP | Controller Problem | Found the reason to be rain water somehow got inside HP LP Cut Out so dried by blower and covered by plastic | 0 |  | Amit, Sanjay, Irwin | Need to ensure rain water does not get into contacts of HP LP Cut Out
14/9/2016 | Nano 10 TR | LL | Low Level | RO Water top up | 0 |  | Hitesh B, Amit | This alarm came due to re-installation of water lines & connections for ICPCVD System
21/9/2016 | MBE 10 TR | LL | Low Level | RO Water top up | 0
21/9/2016 | Dynacool Chiller | LL | Low Level |  | 15 |  | Amit, Hitesh B
|  | LP | Low Pressure
22/9/2016 | MBE 10 TR | LL | Low Level | Water level was found OK after checking so Sensor cleaned | 0 |  | Amit, Ajay, Sanjay
23/9/2016 | MBE 10 TR | LL | Low Level | Water level was found OK after checking so Sensor cleaned | 0 |  | Ajay B

## August 2016
Date | chiller | Fault | issue | solution | downtime (min) | response time ( min) | staff involved | comment
2016-03-08 | Nano 10 TR | LL & CP | Low Level & Controller Problem | RO water top up | 0 | 20 |  | Raju K put entry in Log Book but no further follow up action noted
2016-05-08 | Nano 10 TR | LL | Low Level | RO water top up | 0 | 20 |  | Raju K put off ICMS of Nano Lab during night shift
2016-08-08 | amat 10tr | LL | Low Level | RO water top up | 0 | 20 | HITESH B
2016-11-08 | 1.1 | LL | Low Level | RO water top up | 0 | 40 | Raju K, Irwin
2016-11-08 | Dynacool | LL | Low Level | RO water top up | 0 | 20 | Ajay B
2016-11-08 | Dynacool | LL | Low Level | RO water top up | 0 | 20 | Raju K, Irwin | Sensor cable issue was found to be the reason for LL Alarm coming
17/8/2016 | 1.1 | LL | Low Level | No RO water top up required. Water level was OK | 0 | 10 | Amit, Ajay | Sensor cable found slighthly rusted. Need to be changed.
22/8/2016 | Nano 10 TR | LL | Low Level | RO water top up | 0 | 20 | Sanjay | Alarm came early morning - but still during night shift
23/8/2016 | MBE 10 TR | CP | Controller Problem | low temp fault | 0 | 20 | amit | sensor was seen out of the tank and wate temp was 2 degree
26/8/2016 | Nano 10 TR | LL | Low Level | RO water top up | 0 | 20 | Raju K, Irwin
29/8/2016 | Nano 10 TR | LL | Low Level | RO water top up | 0 | 10 | Ajay B, Irwin

## July 2016
Date | chiller | Fault | issue | solution | downtime (min) | response time ( min) | staff involved | comment
2016-01-07 | Nano 10 TR | LL | Low Level | Topped up water level with 2 buckets of RO Water | 0 | 20 | Hitesh B | Alarm came at 8:10 AM
2016-09-07 | AMAT 10 TR | LL | Low Level | RO Water top up has been done in night shift | 0 | 20 | Raju K
2016-10-07 | AMAT 10 TR | LL | Low Level | RO Water top up has been done on 11/7/2016 in the morning shift | 0 | 720 | Hitesh B, Pawar | Alarm came last night around 8:40 PM but as it was too dark outside to RO water top up was done today morning
2016-12-07 | MBE 10 TR | CP | Comp 1 OL coming on display | Reset the relay | 0 | 10 | Amit, Hitesh B | Alarm came after fitting new HP LP cut out
13/7/2016 | AMAT 10 TR | LL | Low Level | Found water leak at the manifold so removed the pipe and refitted properly with 2 new jubillee clips | 0 | 240 | Raju K, Pawar | This work was not taken up immediately but got completed within the same day
13/7/2016 | MBE 10 TR | CP | Comp 1 OL coming on display | Reset the relay and increased the OL setting of contactor | 0 | 20 | Amit, Pawar, Irwin | No more alarm came after this
25/7/2016 | Nano 10 TR | LL & LP | Alarms came when chiller was switched on after PM completed | Did RO water top up and removed the air from the pump to remove these 2 alarms | 0 | 20 | Hitesh B, Amit Das | This is probably a normal occurrence after completion of a PM
31/7/2016 | Nano 10 TR | PP | Probe Problem | Re-set the display | 0 | 30 | Amit Das | Sometimes it comes due to loose connection of LAN Cable to Display

## June 2016
Date | chiller | Fault | issue | solution | downtime (min) | response time ( min) | staff involved | comment
27/2/2016 | MBE 10 TR | LP | Water pipe came loose at connection inside the chiller | Shut down the chiller and refitted the pipe |  | 45 | Facility
23/2/2016 | 1.1 | LL | Carbon deposit on level sensor cable | Removed the carbon and put back in the tank | 0 | 5 | Amit Das
22/2/2016 | AMAT 10 Tr | LL | 2 coil low | top up water | 0 | 5 | ajay, hitesh
2016-07-02 | AMAT 10 Tr | LL | 2 coil low | top up water | 0 | 15 | powar
2016-07-02 | AMAT 16 Tr | HT |  |  |  |  | powar
2016-08-02 | MBE 10Tr | LP | pump not giving desired pressure | pump has been swap |  |  | amit
21/2/2016 | 1.1 | LL | 2 coil low | top up water |  |  | raju
18/2/2016 | Nano | LL | water pipe burst | fix the pipe | 20 | 10 | ajay
2016-01-03 | Dynacool | HP | Comp trip on R22 High pressure | Dry and wet cleaning of cooling coil done | 20 | 10 | Amit
2016-08-03 | MBE 10 TR | CP | LP fault of comp 1 | R22 top up done | 0 | 60 | Amit
2016-07-04 | AMAT 16 TR | CP | comp 2 OL | reset | 0 | 2 | Amit
2016-08-04 | 1.1 | HT | comp OL | reset | 0 | 5 | Amit
2016-11-04 | 1.1 | LP | RIE passby ON | closed by pass valve | 0 | 10 | Amit
19/4/2016 | AMAT 10 Tr | off | DB MCB trip | Not found | 5 | 5 | Amit
22/4/2016 | Nano | LL | water level low | RO has been top up | 0 | 15 | Raju
27/4/2016 | 1.1 | LP | RIE pass by was kept ON | close the BY pass | 0 | 20 | sandeep
27/4/2016 | MBE 10 Tr | HP |  |  | 0
27/4/2016 | 1.1 | HP |  |  | 0
27/4/2016 | Micro 2 | HP |  |  | 0
28/4/2016 | AMAT 16 Tr | LL |  |  | 0
28/4/2016 | Micro 2 | HP |  |  | 0
2016-02-05 | Dynacool | HT | Temp was maintain at 20 degree instead of 15 degree | MCB has been reset by amit & temp fall to 17 degree | 0 | 10 | amit
2016-03-05 | Nano | LL |  | RO has been top up | 0 |  | raju, hitesh
2016-04-05 | Dynacool | HT | temp not falling below 17 degree | low R407C top has been done | 0 | 288 | irwin amit | Gas not in stock
2016-05-05 | Nano | LL |  | RO has been top up | 0 |  | amit, sanjay, ajay
2016-08-05 | MBE | LL |  | RO has been top up | 0 |  | ajay
2016-08-05 | Dynacool | LL |  | RO has been top up | 0 |  | amit,powar
2016-09-05 | AMAT 16 Tr | LL |  | RO has been top up | 0 |  | Irwin
2016-09-05 | 1.1 | LL |  | RO has been top up | 0 |  | hitesh irwin
2016-08-05 | Dyna cool | LL | Low Level | Remove wire and connect properly | 0 | 10 | Amit,Pawar | 22:30
2016-11-05 | AMAT 16 TR | LL | Low Level | RO has been top up | 0 |  | Sanjay | 13:45
2016-11-05 | NANO 10 TR | LL | Low Level | RO has been top up | 0 |  | Hitesh, Pawar | 13:30
2016-12-05 | AMAT 16 TR | LL | Low Level |  | 0 |  |  | No entry in log book when this occurred. Need to check closely.
2016-12-05 | 1.1 | LL | Low Level |  | 0 |  |  | No entry in log book when this occurred. Need to check closely.
15/5/2016 | MBE lab | CP | Over load trip | Reset Contractor | 0 | 0 | Sanjay,AKD
19/5/2016 | NCPRE | HT | High Temperature | Reset HP LP |  |  |  | Sandeep M
21/5/2016 | MBE 10 TR | CP & HT | PP fault came on display of chiller control panel | Re-soldered loose connection in controller pcb board & installed new sensor cable from control panel to chiller tank |  |  | Amit, SaM, AIR | PP fault is not a minor fault. Compressor will stop working due to PP fault and water temperature will rise. First attempt troubleshooting should be made by quickly switching off and back on the main chiller mcb. Else check for loose connection or change the sensor cable.
19/5/2016 | Nano | LL
22/5/2016 | MBE 5Tr | HP
22/5/2016 | MBE 10 TR | HP
22/5/2016 | 1.1 | LP
23/5/2016 | 1.1 | LP
23/5/2016 | AMAT 10 T | cms off | MBE trip
24/5/2016 | NCPRE | HT
24/5/2016 | M1YR | LP | pump OL trip
25/5/2016 | MBE 5Tr | HP
25/5/2016 | AMAT 16Tr | cp fault | comp 2 OL trip
26/5/2016 | NCPRE | HT | High temp comp | reset HP
30/5/2016 | M1YR | LP | bypass was kept on
2016-01-06 | MBE 10Tr | OL | comp 2 OL trip |  | 0 | 5 | Ajay, Irwin
2016-02-06 | 1.1 | LP | Low Pressure |  | 0
2016-04-06 | 1.1 | LP | Low Pressure
2016-06-06 | MBE 10 Tr | CP/OL | Condenser 1 LP Trip | Re-set HP LP Cut Out | 0 | 5 | Irwin
2016-11-06 | AMAT 16 TR | CP | Pump motor winding gone bad | Getting replacement |  |  | Amit Das, Irwin | Running only on 5TR Compressor so chiller is still partially up.
18/6/2016 | AMAT 10 TR | CP |  |  |  |  | Ajay
19/6/2016 | AMAT 10 TR | CP |  |  |  |  | Hitesh B
20/6/2016 | AMAT 10 TR | CP, LL & LP | Checked and found chiller tank gone almost fully empty so refilled the water and now CP & LL alarm is not coming. LP still to be checked. | Re-filled water tank fully to the top | 0 |  | Hitesh B, Irwin | Need to pay attention to physical condition of chiller - esp. water level in chiller water tank.

## May 2016
Date | chiller | Fault | issue | solution | downtime (min) | response time ( min) | staff involved | comment
2016-02-05 | Dynacool | High Temperature | Temp maintained at 20 degree instead of 15 degree | chiller MCB has been reset by amit & temp fall to 17 degree | 0 | 10 | amit | back up plan of compressor need to be implemented ASAP
2016-03-05 | Nano | water level low |  | RO has been top up | 0 | 20 | raju, hitesh | RO need to be taken from M1 lab
2016-04-05 | Dynacool | High Temperature | temp not falling below 17 degree | low R407C top has been done | 1440 | 288 | irwin amit | Gas not in stock
2016-05-05 | Nano | water level low |  | RO has been top up | 0 | 15 | amit, sanjay, ajay
2016-08-05 | MBE | water level low |  | RO has been top up | 0 | 15 | ajay
2016-08-05 | Dynacool | water level low | level was ok | RO has been top up | 0 | 20 | amit,powar
2016-09-05 | AMAT 16 Tr | water level low |  | RO has been top up | 0 | 15 | Irwin
2016-09-05 | 1.1 | water level low |  | RO has been top up | 0 | 15 | hitesh irwin
2016-08-05 | Dyna cool | water level low | loss connection in the water level sensor | tightened the electrical connections | 0 | 20 | Amit,Pawar
2016-11-05 | AMAT 16 TR | water level low |  | RO has been top up | 0 | 20 | Sanjay
2016-11-05 | NANO 10 TR | water level low |  | RO has been top up | 0 | 20 | Hitesh, Pawar
2016-12-05 | AMAT 16 TR | water level low |  | RO has been top up | 0 | 20
2016-12-05 | 1.1 | water level low |  | RO has been top up | 0 | 15
15/5/2016 | MBE lab | compressor overload | Over load trip | Reset Contractor | 0 | 5 | Sanjay,AKD
19/5/2016 | NCPRE | High Temperature | High Temperature | Reset HP LP | 0 | 25 |  | reset the comp HP cut out
21/5/2016 | MBE 10 TR | Probe problem | PP fault came on display of chiller control panel | Re-soldered loose connection in controller pcb board & installed new sensor cable from control panel to chiller tank | 360 | 10 | Amit, SaM, AIR | PP fault is not a minor fault. Compressor will stop working due to PP fault and water temperature will rise. First attempt troubleshooting should be made by quickly switching off and back on the main chiller mcb. Else check for loose connection or change the sensor cable.
19/5/2016 | Nano | water level low |  |  | 0 | 15
22/5/2016 | MBE 5Tr | High pressure R22 |  | Reset the HP cut out | 0 | 20
19/5/2016 | AMAT 16Tr | water pressure low | Heat exchanger pipe has came out of the chiller tank and tank was MT | Tank has been filled and system was started within 15 mins | 15 | 5
22/5/2016 | MBE 10 TR | High pressure R22 |  | Reset the HP cut out | 0 | 20
22/5/2016 | 1.1 | water low pressure |  | Pressure swich adjusted and reset | 0 | 15
23/5/2016 | 1.1 | water low pressure |  | Pressure swich adjusted and reset | 0 | 15
23/5/2016 | AMAT 10 T | cms off | MBE trip | Reason not understood | 720 | 10 |  | Miscommuncation
24/5/2016 | NCPRE | High Temperature |  |  | 0 | 0
24/5/2016 | M1YR | LP | pump OL trip
25/5/2016 | MBE 5Tr | HP
25/5/2016 | AMAT 16Tr | compressor overload | comp 2 OL trip
26/5/2016 | NCPRE | High Temperature | High temp comp | reset HP
30/5/2016 | M1YR | LP | bypass was kept on
2016-01-06 | MBE 10Tr | compressor overload | comp 2 OL trip
|  |  |  | Total down time of chiller | 2535 | mins
[5 empty] | 42.25 | hrs

## Major Shut Downs
Date | chiller | Fault | issue | solution | downtime (Days) | downtime (Hours) | downtime (mins) | response time ( min) | staff involved | comment
14/3/2016 | Dynacool | High Temperature | Water temperature not maintained stabilized @ set point | Increased condenser fan capacity | 13 |  |  |  |  | Finally issue got resolved by evening of 27/3/2016
2016-04-05 | Dynacool | High Temperature | temp not falling below 17 degree | low R407C top has been done | 1 |  |  | 15 | irwin amit | Gas not in stock, Go for chiller upgradation in order to have a stand by chiller
22/5/2016 | MBE 10 TR | Probe problem | Temperature sensor probe problem (PP) fault came on display of chiller control panel | Re-soldered loose connection in controller pcb board & installed new sensor cable from control panel to chiller tank |  | 6 | 360 | 10 | Amit,Irwin, sandeep | PP fault is not a minor fault. Compressor will stop working due to PP fault and water temperature will rise. First attempt troubleshooting should be made by quickly switching off and ON the main chiller mcb. Else check for loose connection or change the sensor cable.
19/5/2016 | AMAT 16Tr | water pressure low | Heat exchanger pipe has came out of the chiller tank and tank was MT | Tank has been filled and system was started within 15 mins |  |  | 15 | 5 | Pawar, sandeep | users were informed and necessary action were taken by the LIC
23/5/2016 | AMAT 10 Tr | AMAT 10 Tr | AMAT 10 Tr | AMAT 10 Tr |  | 12 | 720 | 10 | Irwin | Delay since no communiation was there, it was just 5 mins job
15/6/2016 | AMAT 10 Tr | AMAT 10 Tr | AMAT 10 Tr | AMAT 10 Tr |  | 8
18/7/2016 | AMAT 16 TR Chiller | PHE Pump Failure |  |  | 2
20/6/2016 | MBE 5 TR Chiller | Compressor Failure | Compressor changed & HP LP Cut Out Changed |  | 3 |  |  |  |  | Issue got resolved on 22/6/2016
21/5/2016 | 1.1 & 1.2 Lab | For PM |  |  | 2
25/7/2016 | Nano 10 TR | For PM |  |  | 2
2016-06-05 | AMAT 10 TR | For PM |  |  | 3
2016-06-05 | AMAT 16 TR | For PM |  |  | 3
26/5/2016 | MBE 5 TR | For PM |  |  | 2
26/5/2016 | MBE 10 TR | For PM |  |  | 2
2016-07-09 | 3rd Floor Chiller - New Building | For PM |  |  |  | 8
15/7/2016 | NCPRE 5 TR | For PM |  |  | 2
2016-12-09 | Dynacool | None but water filter change-out required | To change in line water filter |  |  | 8 |  |  | Amit, Pawar, Hitesh B, Irwin
2016-12-08 | XRD Chiller | Due to Break Down | To change pump head & in line suction water filter |  | 13 |  |  |  |  | Made up on 24/8/2016 by AMC Vendor
30/5/2016 | M1 YR Chiller | For PM |  |  | 1
21/11/2016 | Nano 10 TR | For PM | To flush all the water lines, fill Fresh RO Water into the chiller water tank, change filter inside Y-strainer section, remove faulty pump to give for repair. |  | 0 | 8 |  |  |  | Need to follow up with Thomas [Blu-Berg/Weltech Refrigeration] for repair of faulty water circulation pump
1 & 2/12/2016 | Micro 1 YR 5TR, Micro 1 10 TR | PM has been scheduled
8 & 9/12/2016 | 1.1 & 1.2 Chiller | PM has been scheduled