## Online Data Fill
[6 empty] | [11/9/2015] | [31/3/2016] | [01/04/2016] | [4/4/2016] | [6/4/2016] | [12/4/2016] | [16/4/2016] | [19/5/2016] | [20/5/2016] | [27/7/2016] | [28/7/2016] | [29/7/2016] | [1/8/2016] | [14/9/2016] | [29/9/2016] | [4/10/2016] | [5/10/2016] | [7/11/2016] | [11/11/2016] | [9/2/2017] | [10/3/2017] | [21/4/2017] | [31/5/2017] | [31/7/2017] | [23/8/2017] | [15/9/2017] | [17/11/2017] | [14/12/2017] | [29/1/2018] | [3/5/2018] | [4/5/2018] | [5/5/2018] | [5/5/2018] | [9/5/2018] | [14/5/2018] | [15/5/2018] | [14/6/2018] | [14/6/2018] | [30/6/2018] | [30/6/2018] | [28/7/2018] | [28/7/2018] | [21/8/2018] | [21/8/2018] | [23/8/2018] | [23/8/2018] | [24/8/2018] | [24/8/2018] | [24/9/2018] | [24/9/2018] | [23/10/2018] | [23/10/2018] | [23/10/2018] | [4/12/2018] | [4/12/2018] | [4/12/2018] | [5/1/2019] | [5/1/2019] | [5/1/2019] | [6/2/2019] | [6/2/2019] | [6/2/2019] | [15/3/2019] | [15/3/2019] | [15/3/2019] | [10/4/2019] | [10/4/2019] | [10/4/2019] | [1/7/2019] | [1/7/2019] | [1/7/2019] | [31/8/2019] | [31/8/2019] | [31/8/2019] | [2/9/2019] | [2/9/2019] | [2/9/2019] | [17/9/2019] | [17/9/2019] | [17/9/2019] | [30/10/2019] | [30/10/2019] | [30/10/2019] | [2/11/2019] | [2/11/2019] | [2/11/2019] | [4/11/2019] | [4/11/2019] | [4/11/2019] | [25/11/2019] | [25/11/2019] | [25/11/2019] | [30/11/2019] | [30/11/2019] | [30/11/2019] | [10/12/2019] | [10/12/2019] | [10/12/2019] | [15/1/2020] | [15/1/2020] | [15/1/2020] | [15/2/2020] | [15/2/2020] | [15/2/2020] | [8/8/2020] | [8/8/2020] | [8/8/2020] | [29/11/2020] | [29/11/2020] | [29/11/2020] | [1/2/2021] | [1/2/2021] | [1/2/2021] | [7/4/2021] | [7/4/2021] | [7/4/2021] | [1/5/2021] | [1/5/2021] | [1/5/2021] | [10/6/2021] | [10/6/2021] | [10/6/2021]
Sr. No. | Earthing Station Ref. No. | Serving | Status of Earthing Pit/Station | Scope | Stipulated Max Value (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Comments | Actual Reading (ohms) | Actual Reading (ohms) | Actual Reading (ohms) | Resistance (ohms) | Leakage Current (mA) | Resistance (ohms) | Leakage Current (mA) | Resistance (ohms) | Leakage Current (mA) | Resistance (ohms) | Leakage Current (mA) | Resistance (ohms) | Leakage Current (mA) | Resistance (ohms) | Leakage Current (mA) | Resistance (ohms) | Leakage Current (mA) | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments | Resistance (ohms) | Leakage Current (mA) | Comments
1 | AB1L | Micro 1 Yellow Room | Not Found - so reading taken at copper strip - subject to space availability | IITBNF | 5 | 3.05 | 7.75 | 4.9 | [8 empty] | 2.48 | 2.47 |  | 2.82 |  |  |  | 3.38 | 5.72 | 6.72 | 7.26 B/6.63 A | 7.13 | 3.29 | 3.21 | 2.91 | 4.13 | 4.3 | 1.48 |  |  |  |  | 8.5 |  | 8.01/7.82 |  |  | 2.75 | 30 |  |  | 1.64 | 52.6 |  |  |  |  | 1.73 | 56 | 2.1 | 161.9 |  | 2.29 | 54 | Reading taken at copper strip | 2.65 | 40.4 |  | 2.74 | 69 |  | 2.96 | 38.9 |  | 2.98 | 59.1 |  | 1.56 | 83.9 |  | 2.02 | 66.6 |  |  |  |  | 2.05 | 87.1 |  | 2.1 | 143.7 | [10 empty] | 2.23 | 46.3 |  | 2.23 | 61 |  | 2.87 | 60 |  | 3.05 | 38.7 |  | 2.04 | 24.8 |  | 2.23 | 61 |  | 4.35 | 44 |  | 2.89 | 88.9 |  | 3.02 | 62.3 |  | 2.43 | 31.3
1C |  |  | New Chemical Earthing made | IITBNF | [43 empty] | 3.13 | 42 | [6 empty] | Again covered up due to civil work in Infinite Corridor [23/10/2018] | [29 empty] | 4.35 | 54.3
2 | AB2L | Micro 1 Yellow Room & Micro 1 Evaporators & Chillers | Not Found - so reading taken at copper strip - subject to space availability | IITBNF | 5 | 3.46 |  | 4.75 | [8 empty] | 3.06 | 3.18 |  | 3.34 |  |  |  | 3.74 | 3.91 | 3.95 | 4.11 | 4.6 | 3.46 | 3.42 | 3.43 | 3.84 | 3.7 | 3.83 |  |  |  |  | 4.54 |  |  |  |  | 3.15 | 62.3 |  |  |  |  | 3.36 | 69 |  |  | 3.36 | 39.4 | 3.92 | 105.5 |  | 4.17 | 102 |  | 4.33 | 80.5 |  | 4.57 | 34.6 |  | 4.79 | 92.8 |  | 5.1 | 40.1 |  | 3.35 | 153.1 |  | 3.62 | 56.2 |  |  |  |  | 3.72 | 51.6 |  | 3.85 | 104.8 | [10 empty] | 3.35 | 50.6 |  | 4.06 | 121 |  | 4.39 | 54.8 |  | 4.6 | 87.8 |  | 2.82 | 26.4 |  | 2.35 | 22.1 |  | 2.5 | 117.4 |  | 2.82 | 125.1 |  | 3.25 | 102.6 |  | 2.59 | 143.4
3 | AB3L | XRD (Micro 1 LAB) | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | x | 7.95 | 3.66 | [8 empty] | 2.28 | x |  | 3 |  |  |  | 4.12 | 4.45 | 4.4 | 8.74 | 9.58 | 3.48 | 3.36 | 3.44 | 4.05 | 3.98 | 4.7 | [5 empty] | 9.5 | 9.55 |  |  | 3.44 | 30 |  |  |  |  | 3.63 | 59.6 |  |  | 3.73 | 27.5 | 4.3 | 59 |  |  |  |  | 9.9 | 7.07 |  | 10.31 | 16.38 |  | 10.1 | 13.62 |  | 9 | 13.03 |  |  |  |  | 4.16 | 38.7 |  |  |  |  | 4.21 | 30.2 |  | 4.6 | 60.1 | [10 empty] | 5.25 | 26.2 |  | 5.45 | 92.3 |  |  |  |  | 7.32 | 59.8 |  | 3.87 | 22.1 |  | 5.62 | 12.34 |  | 8.89 | 12.44 |  | 5.02 | 45.3 |  | 5.72 | 30.4 |  | 7 | 11.22
4 | AB4L | XRD (Micro 1 LAB) | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | 0.51 | 4.99 | 2.29 | [8 empty] | 2.72 | 2.98 |  | 3.14 |  |  |  | 4.48 | 5.3 | 5.41 | 5.4 | 5.55 | 3.62 | 3.45 | 3.4 | 4.76 | 4.59 | 3.93 | [5 empty] | 6 | 6.07 |  |  | 3.15 | 60 |  |  |  |  | 3.27 | 120.7 |  |  | 3.47 | 60.1 | 4.57 | 98 |  | 5.63 | 80.8 |  | 6.13 | 46.5 |  | 6.54 | 21.6 |  | 6.8 | 27.5 |  | 7.46 | 31.4 |  |  |  |  | 3.9 | 46.8 |  |  |  |  | 3.96 | 62.1 |  | 4.57 | 51.4 | [10 empty] | 5.06 | 47.4 |  | 6 | 14.93 | [7 empty] | 3.14 | 42.3 |  | 5.28 | 31.3 |  | 5.45 | 92.3 |  | 3.7 | 112.1 |  | 3.8 | 134.7 |  | 4.14 | 64.3
5 | AB5L | EVOSEM (Micro 1 LAB) | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | 3.05 |  | 4.97 | 4.3 | [7 empty] | 2.17 | 2.31 |  | 2.84 |  |  |  | 3.63 | 5.02 | 4.82 | 4.75 | 4.54 | 3.67 | 3.55 | 3.45 | 3.97 | 4.09 | 4.65 | [5 empty] | 4.8 | 4.95 |  |  | 3.4 | 35 |  |  |  |  | 3.68 | 75.8 |  |  | 3.8 | 50.4 | 4.08 | 59.4 |  |  |  |  | 5.46 | 189.4 |  | 5.92 | 29.3 |  | 5.5 | 42.6 |  | 5.02 | 29.3 |  |  |  |  | 3.63 | 41.6 |  |  |  |  | 3.68 | 42 |  | 3.92 | 57.3 | [10 empty] | 4.43 | 43.6 |  | 4.46 | 24 | [7 empty] | 3.83 | 54.1 |  | 4.55 | 18.36 |  | 4.93 | 28.8 |  | 4.65 | 62.5 |  | 4.86 | 48.2 |  | 4.42 | 22.6
6 | AB1R | Raw power LT Panel - First Floor - EE Annex Bldg | Located earlier but need to be dug up again - so reading taken at copper strip - subject to space availability | IIT EMD | 5 | 4.74 |  | 24.8 | [9 empty] | 4.33 |  | 4.42 |  |  |  | 16.17 | 2.64 | 27.5 | 25.8 | 25.6 | 5.24 | 4.13 | 4.76 | 16.34 | 14.94 | 19.62 |  |  |  |  | 23.4 |  |  |  |  | 3.48 | 14 |  |  |  |  | 3.45 | 34 |  |  | 5.6 | 8.4 | 1.88 | 9.72 |  | 24.3 | 6.42 |  | x | x | No Access |  |  | No Access | 2.54 | 4.89 |  |  |  | No Access |  |  | No Access |  |  | No Access | [5 empty] | No Access |  |  | No Access | [11 empty] | No Access |  |  | No Access |  |  | No Access |  |  | No Access |  |  | No Access |  |  | No Access |  |  | No Access |  |  | No Access |  |  | No Access |  |  | No Access
7 | AB2R | Raw power DB - Second Floor - EE Annex Bldg | Located earlier but need to be dug up again - so reading taken at copper strip - subject to space availability | IIT EMD | 5 | 3.8 |  | 6.63 | [9 empty] | 2.87 |  | 3.39 |  |  |  | 4.37 | 5.19 | 5.47 | 5.28 | 7.26 | 3.62 | 2.92 | 3.92 | 5.44 | 5.11 | 6.71 |  |  |  |  | 7.52 |  |  |  |  | 2.25 | 23.5 |  |  |  |  | 2.7 | 67.2 |  |  | 2.02 | 182.3 | 4.06 | 182.5 |  | 4.89 | 5.31 |  | 4.53 | 20.5 |  | 4.71 | 70.1 |  | 5.28 | 73.9 |  | 6.62 | 164.5 |  |  |  |  | 88.5 | 0.18 | Reading suddenly spiked up / gone high |  |  |  | 52.6 | 1.2 | [13 empty] | 13.4 | 1.1 |  | 37.5 | 6.85 |  | 108.6 | 0.48 |  | 89.5 | 0.15 |  |  |  |  | 212 | 0.08 |  | 135.8 | 0.27 |  | 5.75 | 43.4 |  | 5.76 | 30.3 |  | 4.17 | 31.7
8 | AB3R | Organic Electronics Lab | Located earlier but need to be dug up again - so reading taken at copper strip - subject to space availability | IITBNF | 5 | x |  | 8.43 | O.L. | [8 empty] | 2.63 |  | 2.77 |  |  |  | 4.9 | 6.89 | 9.16 | 8.17 | 8.8 | 3.34 | 2.83 | 3.04 | 5.05 | 5.23 | 6.07 |  |  |  |  | 7.89 |  |  |  |  | 2.79 | 14.5 |  |  |  |  | 2.79 | 46.6 |  |  | 3.83 | 60.2 | 4.79 | 60.6 |  | 6.13 | 26.5 |  | 6.97 | 10.92 |  | 6.25 | 16.07 |  | 8.23 | 14.75 |  | 8.36 | 28.5 |  | 3 | 116.8 |  | 3.3 | 79.9 | [25 empty] | 5.64 | 31.7 |  | 6.48 | 16.63 |  |  |  |  | 4.85 | 30.5 |  | 7.22 | 59.5 |  | 7.21 | 34.8 |  | 7.54 | 21.2 |  | 6.7 | 11.81
9 | AB4R | Char 2 Lab | Located earlier but need to be dug up again - so reading taken at copper strip - subject to space availability | [42 empty] | 0.67 | 2.9
9C |  |  | New Chemical Earthing made | IITBNF | [47 empty] | 0.8 | 3.24 |  |  | 7.56 | 4.2 |  | 10.16 | 0.19 |  | 3.73 | 69.3 |  |  |  |  | 15.02 | 2.85 |  |  |  |  | 3.52 | 7.13 |  | 2.9 | 57.7
10 | AB5R | ISL LAB | Located earlier but need to be dug up again - so reading taken at copper strip - subject to space availability | IITBNF | 5 | 3.26 |  |  | O.L.
11 | AB6R | NANO LAB | Not Found - so reading taken at copper strip - subject to space availability | IITBNF | 5 | 3.73 |  | 13 |  |  | 12.72 | 12.82 | [5 empty] | 2.85 |  | 3 |  |  |  | 7.54 | 10.91 | 11.73 | 11.87 | 11.74 | 3.59 | 2.7 | 3.21 | 7.3 | 6.85 | 9.84 |  |  |  |  | 11.92 |  |  |  |  | 2.25 | 33.8 |  |  | 0.41 | 152.2 |  |  |  |  | 0.41 | 84.9 | 0.46 | 243 |  | 0.43 | 85.3 |  | 0.45 | 52.4 |  | 0.43 | 70.8 |  | 0.45 | 98.5 |  | 0.43 | 70.7 |  | 0.41 | 119.1 |  | 0.41 | 56.1 |  |  |  |  | 0.38 | 144.3 |  | 0.42 | 132.3 | [10 empty] | 0.44 | 95.4 |  | 0.45 | 74 |  | 0.43 | 93.4 |  | 0.44 | 37.4 |  | 0.38 | 165.7 |  | 0.46 | 188.9 |  | 0.44 | 175.2 |  | 0.45 | 184 |  | 0.43 | 185.3 |  | 0.43 | 118.9
12 | AB7R | NANO LITHO LAB | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | x |  | 6.91 |  |  | 5.93 | 4 | [5 empty] | 1.85 |  | 2.27 |  |  |  | 4.55 | 4.56 | 4.99 | 5.07 B/3.29 A | 3.67 | 2.12 | 1.94 | 2.07 | 4.52 | 4.88 | 6.13 |  |  |  |  | 7.03 |  | 7.05/3.29 |  |  | 1.85 | 60 |  |  | 0.37 | 41.6 |  |  |  |  | 0.37 | 43.6 | 0.38 | 16.46 |  |  |  | No Access | 0.3 | 68.1 |  | 0.31 | 64.9 |  | 0.32 | 24.1 |  | 0.3 | 56.1 |  | 0.38 | 43.8 |  | 0.33 | 71.9 |  |  |  |  | 0.39 | 65.4 |  | 0.29 | 63 | [10 empty] | 0.32 | 56.2 |  | 0.29 | 37.9 |  | 0.28 | 26.3 |  | 0.32 | 11.74 |  | 0.39 | 30.9 |  | 0.33 | 47.2 |  | 0.32 | 61.2 |  | 0.32 | 25.3 |  | 0.3 | 24 |  | 0.31 | 40
11C |  | New Chemical Earthing made joining 11 & 12 in parallel | RHS Connected Copper Strip to Old Nano Copper Strip & Earth Pit | IITBNF | [43 empty] | 0.43 | 183 | [6 empty] | 0.47 | 92.2 / 221 |  | 0.44 | 97/37.3 |  | 0.44 | 86.7/64.8 |  | 0.43 | 60.1/49.0 | [7 empty] | 0.45 | 43.2/103.3 |  | 0.43/0.46 | 138.6/59.6
|  |  | LHS Connected Copper Strip to Old Nano Litho Copper Strip & Earth Pit | [44 empty] | 0.46 | 134
13 | AB8R | Dis-Connected Earthing Strip/Spare |  | IITBNF | 5 | 2.32 |  | x
14 | AB9R | AMAT LAB | Not Found - so reading taken at copper strip - subject to space availability | IITBNF | 5 | 4.15 |  | 9.35 |  |  | 9.55 | 9.38 | [5 empty] | 2.88 |  | 4.08 |  |  |  | 6.68 | 6.32 | 6.37 | 7.41 B/3.94 A | 5.72 | 4.11 | 3.74 | 3.79 | 5.69 | 5.78 | 6.85 |  |  |  |  | 7.94 |  | 7.96/6.89 |  |  | 2.83 | 48 |  |  |  |  | 2.68 | 91.2 |  |  | 3.1 | 26.9 | 4.1 | 71.4 |  | 5.74 | 26.2 |  | 6.48 | 4.29 |  | 7.05 | 17.05 |  | 7.25 | 19.2 |  | 7.3 | 47.5 |  | 2.1 | 120.2 |  | 3.6 | 63.6 |  |  |  |  | 3.45 | 57.5 |  | 4.54 | 68.9 | [13 empty] | 5.82 | 3.12 |  | 7.26 | 16.97 |  |  |  |  | 3.35 | 43.8 |  | 5.54 | 36.6 |  | 6.45 | 32.4 |  | 5.42 | 49.5 |  | 5.5 | 33.7 |  | 3.84 | 37.9
15 | AB10R | Dis-Connected Earthing Strip/Spare |  | IITBNF | 5 | x |  | x
16 | AB11R | 200 KVA NANO LAB UPS | Re-made chamber with cover | IITBNF | 5 | x |  |  | x |  | 3.7 | - | [11 empty] | 5.25 | 7.9 | 8.51 | 6.92 | 7.5 |  |  |  | Not Accessible | Not Accessible | [73 empty] | 5.05 | 78.3 |  |  |  |  | 5.17 | 85.8 |  | 6.26 | 96.6 |  | 8.25 | 68.3 |  | 7.5 | 86.5 |  |  | 166
17 | AB12R | 300 KVA AMAT LAB UPS | Re-made chamber with cover | IITBNF | 5 | x |  |  | 7.66 |  | 9.62 | 0.23 | [12 empty] | noise | [6 empty] | Not Accessible | Not Accessible | [20 empty] | "Noise" | 178.8 | "Noise" | 226 |  | "Noise" | 184.5 |  | "Noise" | 129.2 |  | "Noise" | 184.5 |  | "Noise" | 137.8 |  | 7.07 | 100.5 |  | "Noise" |  |  | "Noise" | 154.4 | [28 empty] | "Noise" | 153.8 |  |  |  |  | 4.03 | 53.2 |  | 5.94 | 41.4 |  | 9.27 | 61.7 |  | 10.36 | 34.2 |  |  | 111.8
17C |  | New Chemical Earthing made joining 16 & 17 in parallel | New Chemical Earthing Made | IITBNF | [43 empty] | 5.4 | 7.18
18 | NP1 | New Building Both UPS Body Earthing | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | x |  |  | 14 | O.L. | [9 empty] | 5.05 |  |  |  | O.L. | O.L. | O.L. | O.L. | O.L. | O.L. | 930 | 840 | 342 | 223 | 730 | [9 empty] | O.L. | 0.1 |  |  |  |  | O.L. | 0.1 |  |  | 1220 | 0 | 630 | 0.1 |  |  |  |  | O.L. | 0.17 |  | O.L. | 0.12 | [10 empty] | O.L. | [20 empty] | 10.25 | 13.53 | Inside New Bldg UPS Room - on Earth Strip | [6 empty] | 11.22 | 6.45 | Inside New Bldg UPS Room - on Earth Strip |  |  |  | 5.69 | 60.9 |  | 5.3 | 62.5 |  | 6.45 | 68.3 |  | 7.24 | 63.6 |  | 0.43 | 80
19 | NP2 | New Building Both UPS Body Earthing | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | x |  |  | 25 | O.L. | [9 empty] | 16.4 |  |  |  | O.L. | x | x | x | x | x | x | x | x | x | [43 empty] | x | [20 empty] | 65.5 | 57.3 | Inside New Bldg UPS Room - on Earth Strip | [6 empty] | 10.89 | 6.4 | Inside New Bldg UPS Room - on Earth Strip |  |  |  | 5.5 | 62.2 |  | 7.2 | 58.6 |  | 15.03 | 9.24 |  | 6.8 | 63.3 |  | 1.22 | 60
20 | NP3 | General Purpose Lift [?] | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | x |  |  |  | O.L.
21 | NP4 | IT Server Room | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | 78.6 |  |  |  | O.L.
22 | NP5 | IT Server Room | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | 1100 |  |  |  | O.L.
23 | NB1 | MBE/1.1&1.2/NCPRE LAB (2nd Floor)/NCPRE DC LAB (3rd Floor) | Pit is visible but reading has to be taken at copper strip | IITBNF/NCPRE | 5 | 3.45 |  |  | 4.13 |  | 1.73 |  | 2.85 | 2.12 | 3.48 |  |  | 3.94 |  | 3.47 |  |  |  | 4.07 | 0.22 | 0.22 | 0.21 | 3.96 | 3.81 | 0.19 | 3.8 | 4.48 | 4.45 | 4.64 |  | 3.7 | 3.25 | After Salt Water Treatment done on 4/5/2018 | [5 empty] | 3.28 | 18.65 |  |  |  |  | 3.59 | 35.5 |  |  | 4.02 | 35 | 2.94 | 48 | After salt water treatment done last week by Rajendra S & Hitesh B | 3 | 41.2 |  | 3.14 | 11.36 |  | 3.29 | 12.73 | Watering & Salt Treatment Done. New Readings need to be taken this week. | 3.31 | 32.8 |  | 3.19 | 33.3 |  | 2.97 | 39.7 |  | 3.38 | 13.41 |  | 3.14 | 13.53 | After 1 kg salt & water added | 3.61 | 20 |  | 4.04 | 33 |  | 0.37 | 11.3 | After 1 kg salt & water added | 3.33 | 22 |  |  |  |  | 3.25 | 14.17 |  | 3.52 | 8.64 |  | 4.99 | 16.25 |  | 4.82 | 11.62 |  | 3.79 | 12.84 |  | 4.68 | 7.6 |  | 4.75 | 9.23 |  | 4.43 | 9.23 |  | 4.32 | 7.23 |  | 3.54 | 17
|  | New copper strip for NCPRE FAB LAB Tapped from No. 1 | Pit is visible but reading has to be taken at copper strip | [5 empty] | 0 | [57 empty] | Watering & Salt Treatment Done. New Readings need to be taken this week.
24 | NB2 | New Building Lightning Protection System (LPS) | Pit is visible but reading has to be taken at copper strip | IITBNF | 10 | 438 |  |  | 1060 |  | 293 | 210 | 262 | 259 | 57.5 |  |  | 17.16 |  | 162.6 |  |  |  | 355 | 464 | 496 | 1180 | 970 | 48 | 0.24 | 180 | 8.23 | 1.49 | 8.54 |  | 7.28 | 7.04 | After Salt Water Treatment done on 4/5/2018 | [5 empty] | 4.24 | 11 |  |  |  |  | 4.68 | 15.44 |  |  | 7.6 | 8.15 | 9.85 | 7.13 | After salt water treatment done last week by Rajendra S & Hitesh B | 22.7 | 2.22 |  | 6.79 | 3.06 |  | 23.5 | 1.73 | Watering & Salt Treatment Done. New Readings need to be taken this week. | 19.7 | 1.21 |  | 14.9 | 2.19 |  | 4.43 | 10.57 |  | 7.39 | 5.2 |  | 17.96 | 0.89 | Reading went up. Not possible to do salt water treatment of earth pit in absence of MBE Student Group as their system is there. | 10.93 | 1.91 |  | 720 | 0.07 | Reading has gone much higher than last month's Reading | 0.16 | 0.08 | After 1 kg salt & water added | 920 | 0.09 |  |  |  |  | O.L. | 0 |  | O.L. | 0 |  |  |  |  | 145 | 0 |  | 163.2 | 0.24 |  |  | 0 |  |  | 0 | OL showing on display |  | 0 | OL showing on display |  | 0 | OL showing on display | 1280 | 0
25 | NB3 | New Building 3rd & 5th Floor LABS | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | 4.32 |  |  | 5.93 |  | 0.46 | 0.43 | 4.34 | 4.28 | 4.61 |  |  | 5.34 |  | 4.46 |  |  |  | 5.64 | 5.76 | 5.93 | 6.25 B/3.92 A | 4.83 | 5.42 | 5.08 | 5.56 | 6.83 | 6.93 | 7.32 |  | 3.62 | 3.14 | After Salt Water Treatment done on 4/5/2018 | [5 empty] | 4.43 | 18 |  |  |  |  | 4.6 | 18.24 |  |  | 4.69 | 30.3 | 3.23 | 59.3 | After salt water treatment done last week by Rajendra S & Hitesh B | 4.66 | 20.8 |  | 4.47 | 8.75 |  | 5.55 | 6.37 | Watering & Salt Treatment Done. New Readings need to be taken this week. | 6.02 | 16.37 |  | 6.04 | 15.06 |  | 4.23 | 28.6 |  | 5 | 11.08 |  | 4.29 | 7.84 | After 1 kg salt & water added | 4.73 | 17.04 |  | 5.71 | 15.24 |  | 0.16 | 6.86 | After 1 kg salt & water added | 4.5 | 11.88 |  |  |  |  | 4.85 | 16.78 |  | 4.92 | 6.55 |  |  |  |  | 6.6 | 7.42 |  | 5.05 | 7.46 |  | 7.42 | 3.81 |  | 8.13 | 3.78 |  | 3.81 | 12.44 |  | 4.97 | 7.81 |  | 4.08 | 17.43
26 | NB4 | New Building NCPRE Lab Service Corridor Stabilizers Earthing | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | 5.5 |  |  | 6.53 |  | 5.21 | 4.56 | 4.53 | 5.52 | 5.25 |  |  | 5.7 |  | 5.46 |  |  |  | 8.27 | 4.56 | 4.95 | 5.43 B/4.89 A | 5.1 | 5.75 | 5.37 | 5.82 | 8.76 | 8.33 | 9.45 |  | 7.41 | 5.27 | After Salt Water Treatment done on 4/5/2018 | [5 empty] | 5.53 | 8 |  |  |  |  | 5.61 | 18.3 |  |  | 6.05 | 10.64 | 4.58 | 30.2 | After salt water treatment done last week by Rajendra S & Hitesh B | 4.31 | 27.2 |  | 4.52 | 4.54 |  | 4.53 | 12 | Watering & Salt Treatment Done. New Readings need to be taken this week. | 4.29 | 16.37 |  | 4.42 | 10.14 |  | 4.21 | 19.28 |  | 5.47 | 4.84 |  | 3.94 | 9.21 | After 1 kg salt & water added | 4 | 6.21 |  | 6.87 | 9.84 |  | 0.06 | 1.96 | After 1 kg salt & water added | 5.17 | 13.67 |  |  |  |  | 4.94 | 12.08 |  | 5.08 | 5.89 |  |  |  |  | 5.55 | 7.48 |  | 5.6 | 10.04 |  | 8.73 | 6.29 |  | 8.65 | 6.56 |  | 5.52 | 4.82 |  | 5.43 | 4.79 |  | 4.18 | 11.67
27 | NB5 | New Building 3.2 Floor LAB | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | 5.41 |  |  | 6.14 |  | 4.37 |  | 4.74 | 4.6 | 5.05 |  |  | 5.36 |  | 5.06 |  |  |  | 5.4 | 5.46 | 4.71 | 4.85 | 4.64 | 4.16 | 3.96 | 4.25 | 5.98 | 5.72 | 7.4 |  | 7.74 |  | After Salt Water Treatment done on 4/5/2018 | [5 empty] | 5.25 | 9 |  |  |  |  | 5.77 | 9.02 |  |  | 5.69 | 22.3 | 4.33 | 30.1 | After salt water treatment done last week by Rajendra S & Hitesh B | 4.52 | 25.1 |  | 5.5 | 18.95 |  | 5.5 | 18.95 | Watering & Salt Treatment Done. New Readings need to be taken this week. | 4.37 | 26.1 |  | 4.64 | 43.6 |  | 0.24 | 24.9 |  | 5.43 | 9.22 |  | 4.65 | 20.7 | After 1 kg salt & water added | 4.92 | 9.87 |  | 6.03 | 15.92 |  | 3.91 | 15.07 | After 1 kg salt & water added | 5 | 32.6 |  |  |  |  | 4.77 | 22.7 |  | 4.02 | 6.2 |  |  |  |  | 5.52 | 14.6 |  | 5.55 | 18.82 |  | 7.15 | 27.7 |  | 7.12 | 10.58 |  | 5 | 7.95 |  | 6.55 | 13.39 |  | 4.4 | 13.62
28 | NB6 | New Building General Purpose Lift | Pit is visible but reading has to be taken at copper strip | IIT | x | x
29 | ABRS1 | Micro LABS 1 & 2 300 KVA UPS & LT Panel | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | x |  |  | 0 | [10 empty] | 0 |  |  |  | 0.46 | 0.12 | 0.19 | 0.14 | [49 empty] | 0.16 | 1.87
30 | ABRS2 | Micro LABS 1 Nordiko Furnace Corner/Side - All Instruments/Micro 2 AHU | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | x |  | 0.14 | 0.14 | [7 empty] | 0.13 | [6 empty] | 0.13 | 0.14 |  | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14
31 | ABRS3 | XPS | Pit is visible but reading has to be taken at copper strip | IITBNF | 0.4 | 2.15 |  |  | 0.12 | [6 empty] | 0 |  |  | 0.63 |  | 0.65 | 0.6 | 0.65 | 0.65 | 0 | 0 | 0 |  |  |  | 0.96 | 0.003 | 0.07 |  |  |  | 0.11 | [6 empty] | 0 | 7.62 |  |  |  |  | 1.23 | 7.72 | [10 empty] | 0 | 6.15 | [19 empty] | 0 | 6.89 |  | 0 | 6.07 | [10 empty] | 0 | 6.15 | [19 empty] | 0.81 | 59.4
|  | XPS Old Earthing | Pit is visible but reading has to be taken at copper strip | [5 empty] | 1.79 |  | 1.95 |  | 2.07 | 1.66 |  | 1.61 |  |  | 1.94 | 1.99 |  |  |  | 1.94 | 2.14 | 2.1 | 2.17 | 2.31 | 1.74 | 1.84 | 1.93 | 2.53 | 2.65 | 3.52 |  |  | 2.11 | [6 empty] | 2.1 | 27.5 |  |  |  |  | 2.35 | 69.4 |  |  | 2.48 | 59 | 2.17 | 90.5 |  | 2.83 | 66.9 |  | 2.9 | 48 |  | 2.95 | 48 |  | 2.95 | 40.5 |  | 3.09 | 50.7 |  | 1.65 | 85.6 |  | 2.5 | 44.7 |  |  |  |  | 2.62 | 48.1 |  | 2.73 | 64.8 | [7 empty] | 3.18 | 21.8 | Salt Water Treatment done after readings taken | 2.14 | 46.8 |  | 2.48 | 20.3 |  | 2.87 | 39.9 |  | 2.65 | 21.6 | Watering done 1 day before | 2.7 | 29.5 |  |  | 0 | Earth Strip Disconnected from Earthing Station
|  | XPS New Earthing | Pit is visible but reading has to be taken at copper strip | [5 empty] | 0.74 |  | 0.79 |  | 0.86 | 0.76 |  |  |  | 0.75 | 0.87 |  |  |  |  | 0.91 | 0.95 | 0.96 | 1.08 | 1.01 | 0.89 | 0.94 | 1 | 1.07 | "noise" | 1.26 | [15 empty] | 1.02 | 107.2 |  |  | 1.07 | 146.5 | 0.95 | 157.3 |  | 0.99 | 116.3 |  | 1.08 | 90.8 |  | 1.09 | 63.9 |  | 1.1 | 84.7 |  | 1.12 | 76.7 |  | "Noise" | 27.9 |  | 1 | 88 |  |  |  |  | 1.1 | 84.7 |  |  | 144 | [10 empty] | x | 68 | Noise came on display | 1.03 | 25.7 |  | 1.12 | 61.3 |  | 1.07 | 23.9 | Watering done 1 day before | 0.94 | 45.5 |  | 1.15 | 30.8 |  | 1.29 | 59.1 |  |  |  |  | 1.17 | 34.3 |  | 0.86 | 50.6
36 | Micro 2 Lab Common Earthing | [18 empty] | 38.6 |  |  |  | 45.2 | 49.9 | 48.9 | 49.6 | 48 | 45.5 | 45.5 | 41.7 | 46.2 | 44.4 | 47.5 | [5 empty] | 49 | 50 |  |  | 48 | 1.17 |  |  | 44.1 | 0.85 |  |  |  |  | 1.58 | 70
36C | Micro 2 Lab Common Earthing |  | New Chemical Earthing Made | IITBNF | [43 empty] | 1.64 | 60 | [6 empty] | 1.74 | 116 |  | 1.86 | 212 |  | 1.9 | 45.6 |  | 1.85 | 37 |  | "Noise" | 102 |  | 2.26 | 79.2 |  | "Noise" | 86.3 |  | 2.14 | 43.3 |  |  |  |  | 2.62 | 32.9 |  | 1.98 | 55.2 | [10 empty] | 1.66 | 57.6 |  |  | 1.52 | 40.8 | 1.68 | 58 |  | 1.6 | 63 | Watering done 1 day before |  |  |  | 2.22 | 29.4 |  | 2.5 | 29.8 |  | 2 | 59.5 |  | 2.13 | 102.7 |  | 2 | 37.6
32 | ABRS4 | Micro 1 Yellow Room AHU | Pit is visible but reading has to be taken at copper strip | IITBNF | 5 | 1340
33 | ABRS5 | New Building Ground Floor LT Panel | Pit is visible but reading has to be taken at copper strip | IIT | 5 | x
34 | ABRS6 | New Building Ground Floor LT Panel | Pit is visible but reading has to be taken at copper strip | IIT | 5 | x
35 |  | New AJA System Dedicated Earthing Stations in front of Nano E Bldg |  | IITBNF | [30 empty] | 1.07 |  | 1.21 |  |  |  |  | 1.98 | 48.1 | [8 empty] | 2.52 | 48.6 | 2.59 | 94.4 | 2.53 | 103.8 |  | 2.95 | 68.6 |  | 3.11 | 24.9 |  | 2.36 | 54.1 |  | 2.32 | 50.2 |  |  |  |  | 0.29 | 54.1 |  | 2.64 | 15.91 |  |  |  |  | 1.94 | 39.2 |  | 2.89 | 31.4 | [10 empty] | 3.43 | 35.3 |  |  | 3.6 | 29.7 | 3.89 | 26 |  | 3.83 | 25.7 |  | 2.72 | 58.6 |  | 2.25 | 62.1 |  | 2.6 | 32.1 |  | 2.22 | 48.2 |  | 2.36 | 21.4 |  | 2.23 | 51.5
36 |  | Dynacool [New] |  | IITBNF | [99 empty] | 7.7 | 54.1 | [10 empty] | 6.37 |  |  | 7.23 | 22.8
37 |  | Dynacool [Dedicated - Newly Made] |  | IITBNF | [111 empty] | 1.62 |  |  | 2 | 133.3
38 |  | DG Set Neutral 1 |  | IITBNF | [103 empty] | 9.75 | 1.05 | [6 empty] | 7.55 | 0.79 |  | 7.72 | 1.08 |  | 6.65 | 1.27 |  | 6.17 | 2.43
39 |  | DG Set Neutral 2 |  | IITBNF | [103 empty] | 9.74 | 1.1 | [6 empty] | 7.73 | 0.65 |  | 7.72 | 1.01 |  | 6.65 | 1.35 |  | 6.17 | 2.39

## Lab Wise Critical Tools Reading
| Date | 31/10/2019 |  | 26/11/2019 |  | 2019-10-12 |  | 16/2/2020 |  |  | 2020-08-08 |  | 29/11/2020 |  | 2021-01-02 |  | 2021-07-04 |  | 2021-01-05 |  | 2021-06-06
NANO LAB |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA)
1 | ATC Sputter | 0.15 | 14.11 | 0.16 | 11.6 | 0.16 | 11.98 | 0.17 | 6.84 |  | 0.2 | 17.9 | 0.18 | 12.05 | 0.18 | 18 | 0.22 | 6.22 | 0.13 | 3.49 | 0.21 | 5.76
2 | Orion Sputter | 0.08 | 6 | 0.1 | 5.09 | 0.1 | 5.28 | 0.11 | 3.75 |  | 0.11 | 11.75 | 0.12 | 6.13 | 0.12 | 6.71 | 0.13 | 3.35 | 0.13 | 3.28 | 0.12 | 3.22
3 | ALD | 0 | 39.1 | 0.02 | 43.1 | 0.02 | 20.2 | 0.02 | 30.3 |  | 0.03 | 53.2 | 0.06 | 8.77 | 0.05 | 36.2 | 0.03 | 29.4 | 0.03 | 13.34 | 0.03 | 12.59
4 | ALD Load Lock | 0.03 | 30.1 | 0.03 | 21.9 | 0.03 | 19.5 | 0.03 | 19.16 |  | 0.03 | 61.8 | 0.04 | 45.5 | 0.04 | 53.9 | 0.04 | 19.41 | 0.03 | 28.6 | 0.04 | 19.26
5 | ICPCVD | 0.03 | 66 | 0.03 | 26.5 | 0.04 | 54.5 | 0.04 | 53 |  | 0.04 | 103.3 | 0.07 | 36.2 | 0.06 | 58.1 | 0.06 | 49.5 | 0.06 | 53.5 | 0.05 | 39.7
6 | RTP | 0.11 | 4.05 | 0.11 | 5.7 | 0.11 | 7.53 | 0.11 | 5.63 |  | 0.18 | 2.69 | 0.16 | 5.19 | 0.15 | 9.7 | 0.17 | 2.47 | 0.17 | 4.48 | 0.16 | 3.71
NANO LITHO LAB |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA)
1 | RAITH | 0.29 | 63 | 0.32 | 56.2 | 0.38 | 16.46 | 0.32 | 11.74 |  | 0.39 | 30.9 | 0.33 | 47.2 | 0.32 | 61.2 | 0.32 | 25.3 | 0.3 | 24 | 0.31 | 40
2 | DSA
MBE LAB |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA)
1 | MBE 1 - Subho Sir System | [9 empty] | 3.79 | 12.84 | 4.68 | 7.6 | 4.71 | 9.23 | 4.7 | 9.5 | 4.32 | 7.23
2 | MBE 2 - Laha Sir System | [9 empty] | 3.79 | 12.84 | 4.68 | 7.6 | 4.71 | 9.23 | 4.7 | 9.8 | 4.32 | 7.23
3 | MBE 3 - SSM Sir System
4 | MBE 4 - Subho Sir System - New Expected | System still awaited | [5 empty] | 0.39 | 57.5 | System Arrived & Installed | 0 | 15.44 | [6 empty] | 0.9 | 1.77
1.1&1.2 Lab - New Bldg |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA)
1 | PDS | 0.24 | 112.5 | 0.29 | 128.9 | 0.28 | 76.6 | 0.29 | 78.6 |  | 0.33 | 32 | 0.38 | 37.8 | 0.34 | 47.5 | 0.34 | 56.1 | 0.34 | 57.2 | 0.44 | 65
2 | 1.1 RIE | 0.12 | 4.38 | 0.08 | 51.3 | 0.13 | 8.74 | 0.14 | 35 |  | 0.14 | 6.16 | 0.15 | 3.31 | 0.13 | 14.56 | 0.06 | 57 | 0.15 | 80.9 | 0.14 | 34.1
3 | Nano RIE | 0.06 | 21.9 | 0.04 | 17.15 | 0.1 | 21.6 | 0.08 | 157.2 |  | 0.14 | 7.25 | 0.12 | 12.8 | 0.12 | 112.2 | 0.11 | 142.8 | 0.11 | 160.8 | 0.11 | 24.8
4 | Plasma Asher | 0.36 | 62 | 0.64 | 56.9 | 0.55 | 35 | 0.34 | 123.7 |  | 0.17 | 6.59 | 0.38 | 144.8 | 0.38 | 71 | 0.37 | 71.7 | 0.39 | 72.4 | 0.39 | 130.7
5 | Ar-Ion Milling System | 0.34 | 319 | 0.36 | 448 | 0.35 | 360 | 0.37 | 0.429 |  | 0.39 | 309 | 0.38 | 464 | 0.38 | 397 | 0.43 | 227 | 0.4 | 244 | 0.43 | 463
6 | Ar Annnealing System
7 | AJA System | 2.89 | 31.4 | 3.4 | 31.1 | 3.6 | 29.7 | 3.83 | 25.7 |  | 1.68 | 43.7 | 2.63 | 31.8 | 2.6 | 35.2 | 2.22 | 48.2 | 2.36 | 33.7 | 2.16 | 19.33
MICRO 2 Lab |  | R (ohms) | Leakage (mA) |  |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA)
1 | XPS Set Up | 0 | 6.07 | 0 | 6.16 | [5 empty] | 0.35 | 153 | 0 | 65 | 0 | 65 | 0 | 71 | 0 | 6.08 | 0 | 61
MICRO 1 Lab |  | R (ohms) | Leakage (mA) |  |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA)
1a | XRD System | 4.6 | 60.1 | 5.06 | 47.4 | 5.45 | 92.3 |  |  |  | 3.87 | 22.1 | 5.62 | 12.34 | 8.89 | 12.44 | 5.02 | 45.3 | 5.72 | 30.4 | 7 | 11.22
1b | XRD System | 4.57 | 51.4 | 5.25 | 26.2 | 6 | 14.93 |  |  |  | 3.14 | 42.3 | 5.28 | 31.3 | 5.54 | 92.3 | 3.7 | 112.1 | 3.8 | 134.7 | 4.14 | 64.3
2 | EVOSEM System | 3.92 | 57.3 | 4.43 | 43.6 | 4.46 | 24 |  |  |  | 3.83 | 54.1 | 4.55 | 18.36 |  |  | 4.65 | 62.5 | 4.86 | 48.2 | 4.42 | 22.6
[11 empty] | 2.82 | 26.4
MICRO 1 YELLOW ROOM |  | R (ohms) | Leakage (mA) |  |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) |  | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA)
1 | STSRIE | 2.05 | 87.1 | 2.23 | 46.3 | 2.23 | 61 | 3.05 | 38.7 |  | 2.04 | 24.8 | 2.23 | 61 | 4.35 | 44 | 2.89 | 88.9 | 0.57 | 160.8 | 0.68 | 145.4
2 | OERLIKON SYSTEM | 2.05 | 87.1 | 2.23 | 46.3 | 2.23 | 61 | 3.05 | 38.7 |  | 2.04 | 24.8 | 2.23 | 61 | 4.35 | 44 | 2.89 | 88.9 | 0.7 | 207 | 0.57 | 106.6
CHAR 2 LAB | [12 empty] | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA) | R (ohms) | Leakage (mA)
1 | DYNACOOL PPMS Set Up | [11 empty] | 1.84 | 45.8 | 1.62 | 45.8 | 2 | 133.3
NCPRE FAB LAB

## Facility Support Systems Earthi
16/2/2020
Sr. No. | Facility Item Description | R (ohms) | Leakage (mA) | Comments
1 | Nano (& Nano Litho) AHU
Nano AHU Main Cable
| Nano AHU Control Panel | 0.05 | 154.5
Nano AHU Main Blower Motor
Nano AHU Condenser Unit 1
Nano AHU Condenser Unit 2
Nano AHU Condenser Unit 3
Nano AHU Condenser Unit 4
Nano AHU Condenser Unit 5
2 | AMAT AHU
AMAT AHU Main Cable
| AMAT AHU Control Panel | 68 | 0 | High Earthing Resistance
AMAT AHU Main Blower Motor
AMAT AHU Condenser Unit 1
AMAT AHU Condenser Unit 2
AMAT AHU Condenser Unit 3
AMAT AHU Condenser Unit 4
3 | 1.1&1.2 Lab AHU - New Bldg
Main Cable
| Control Panel | 0.07 | 1126
Main Blower Motor
| Condenser Unit 1 | 0.34 | 3.56
| Condenser Unit 2 | 0.34 | 3.17
| Condenser Unit 3 | "Noise" | 1482
4 | MBE Lab AHU - New Bldg
| Main Cable | 68.6 | 1.76 | High Earthing Resistance
Control Panel
Main Blower Motor
| Condenser Unit 1 | 0.94 | 0.9
| Condenser Unit 2 | 0.94 | 0.86
| Condenser Unit 3 | 68.8 | 0.46 | High Earthing Resistance
5 | 2nd Floor NCPRE Fab Lab AHU - New Bldg
Main Cable
Control Panel
Main Blower Motor
Condenser Unit 1
Condenser Unit 2
Condenser Unit 3
| TFAU Control Panel |  |  | Newly Added & Made Operational on 6/3/2020
TFAU Main Power Supply Cable
TFAU Blower Motor
TFAU Condenser Unit [5.5 TR]
6 | AMAT 10 TR Chiller
| Control Panel | 103 | 0 | High Earthing Resistance
7 | AMAT 16 TR Chiller
Control Panel
8 | Nano 10 TR Chiller
| Control Panel | 109 | 0 | High Earthing Resistance
9 | MBE UPS DG Set/AMF Panel Emergency Change-Over [By-Pass Arrangement]
| Manual By-Pass Change-Over Panel | 0.04 | 91.5