## Equipment List
Scope: | IITBNF - List of Exhaust Systems | [8 empty] | Actual reading Foot per Minute ( FPM) | Actual reading Foot per Minute ( FPM) | Actual reading Foot per Minute ( FPM) | Actual reading Foot per Minute ( FPM) | Actual reading Foot per Minute ( FPM) | Actual reading Foot per Minute ( FPM) | Actual reading Foot per Minute ( FPM) | Actual reading Foot per Minute ( FPM) | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) | Actual reading Foot per Minute ( FPM) | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM) |  | Actual reading Foot per Minute ( FPM)
|  | Comments | Exhaust Pipe Diameter | Exhaust Pipe Diameter | Exhaust Blower Motor Specification | Additional Remarks | CFM spec | FPM spec | Tool connected | 2016-09-01 | 2017-05-01 | 2017-06-21 | 2017-07-07 | 2017-07-14 | 2017-08-17 | 2017-08-31 | 2018-05-31 | 2018-08-27 | Comments - 27 August 2018 | 25/9/2018 | Comments - 25/9/2018 | 22/10/2018 | 2018-03-12 | 2019-09-01 | Name of the tool | 2019-11-03 | Name of the tool | 31/8/2019 | Name of the tool | 17/9/2019 | Name of the tool | 31/10/2019 | Name of the tool | 30/11/2019 | 2019-10-12 |  | 14/1/2020 | 15/2/2020 |  | 18/8/2020 |  | 29/11/2020 |  | 24/2/2021 |  | 2021-08-04 |  | 2021-01-05 |  | 2021-10-06
Sr. No. | Area/System |  | @ Blower Side | @ Tool / System End Side
1 | NANO SERVICE CORRIDOR
a | Nano Litho Exhaust |  | 7" @ outlet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2016-09-01: 4650; 2017-06-21: 1626; 2017-08-17: 1795; 2018-05-31: 1824; 2018-08-27: 803 |  | 1901 |  | 1940 | 1616 | 1940 | Exhaust-Nano litho lab- laminar flow bench & DSA | 1767 | Exhaust-Nano litho lab- laminar flow bench & DSA | 1822 |  | 1458 | Exhaust-Nano litho lab- laminar flow bench & DSA | 1815 | Exhaust-Nano litho lab- laminar flow bench & DSA | 1813 | 2015 |  | 2082 | 2027 |  | 2091 |  | 2494 |  | 1635 |  | 1470 |  | 1601 |  | 1593
| Nano Litho Stand-By Exhaust | [32 empty] | 444.4 | 401.9 |  |  | 282 |  | 489 |  | 0 | Motor Winding gone bad - mcb in DB found tripped | 0 | OFF. [Motor was replaced on 17 Dec 2020] | 0 | OFF | 0 | OFF | 0 | OFF
b | ALD & ALD LL Exhaust |  | 7" @ outlet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2016-09-01: 3199; 2017-06-21: 1274; 2017-08-17: 1322; 2018-05-31: 1354; 2018-08-27: 826 |  | 1379 |  | 1389 | 1370 | 1370 | Exhaust- Nano lab-ALD | 1249 | Exhaust- Nano lab-ALD | 1234 |  | 2679 | Exhaust- Nano lab-ALD | 1257 | Exhaust- Nano lab-ALD | 1216 | 1104 |  | 2350 | 1237 |  | 1230 |  | 904.2 |  | 1242 |  | 1201 |  | 1094 |  | 1146
c | Nano Lab CVD Scrubber & Gas Cabinet Exhaust |  | 6" @ outlet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2016-09-01: 525; 2017-06-21: 957; 2017-08-17: 2551; 2018-05-31: 3003; 2018-08-27: 950 |  | 3131 |  | 2633 | 3131 | 3190 | Exhaust-Nano lab-CVD scrubber/gas cabinet | 2353 | Exhaust-Nano lab-CVD scrubber/gas cabinet | 2454 |  | 2318 | Exhaust-Nano lab-CVD scrubber/gas cabinet | 2373 | Exhaust-Nano lab-CVD scrubber/gas cabinet | 2239 | 2284 |  | 2153 | 2141 |  | 2296 |  | 2045 |  | 2001 |  | 2050 |  | 2176 |  | 2041
d | Nano Lab Furnace Exhaust |  | 6" @ outet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 1824 |  | 4727 |  |  | 4804 | 4595 | 5182 | 834 |  | 5005 |  | 4765 | 5159 | 5159 | Exhaust- Nano lab-ultech furnaces | 4558 | Exhaust- Nano lab-ultech furnaces | 4109 |  | 4454 | Exhaust- Nano lab-ultech furnaces | 4454 | Exhaust- Nano lab-ultech furnaces | 4552 | 4540 |  | 3063 | 3623 |  | 4257 |  | 3125 |  | 0 | OFF | 3020 |  | 4051 |  | 3731
e | New Wet Bench Exhaust | Newly Installed |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | Dedicated Exhaust for this Wet Bench has been installed |  | 100 |  | 2017-06-21: 1061; 2017-08-17: 1801; 2018-05-31: OFF; 2018-08-27: 0 | OFF | OFF |  |  | 1763 |  | Exhuast-Nano lab-wet bench | off | Exhuast-Nano lab-wet bench | 0 | OFF | 0 | Exhuast-Nano lab-wet bench | 1644 | Exhuast-Nano lab-wet bench | 0 | 0 |  | 0 | 0 |  | 1583 |  | 0 | OFF | 0 | OFF | 0 | OFF | 0 | OFF | 0 | OFF
[5 empty] | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
2 | AMAT SERVICE CORRIDOR |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
a | Pump Exhaust |  | 6" @ outlet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 3100 | 150 | 232 |  | 1660 | 785 |  | 921 | 429 |  | 232 |  | 358 | 488 | 694 | Exhaust-AMAT Lab- pumps | off | Exhaust-AMAT Lab- pumps | 0 | OFF | 0 | Exhaust-AMAT Lab- pumps | 0 | Exhaust-AMAT Lab- pumps | 0 | 0 |  | 0 | 150.9 |  | 0 |  | 0 | OFF | 0 | OFF | 0 | OFF | 0 | OFF | 0 | OFF
b | AMAT Gas Cabinet Exhaust |  | 7.5" @ outlet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2016-09-01: 875; 2017-06-21: 2109; 2017-08-17: 2101; 2018-05-31: 2338; 2018-08-27: 690 |  | 972 |  | 2226 | 2310 | 2367 | Exhaust-AMAT Lab- Gas cabinet | 2138 | Exhaust-AMAT Lab- Gas cabinet | 2245 |  | 2318 | Exhaust-AMAT Lab- Gas cabinet | 2115 | Exhaust-AMAT Lab- Gas cabinet | 2104 | 2124 |  | 2125 | 2026 |  | 2141 |  | 2156 |  | 2144 |  | 1915 |  | 2055 |  | 2001
c | Nano Lab RTP ICPCVD Exhaust |  | 6" @ outlet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2016-09-01: 2155; 2017-06-21: 951; 2017-08-17: 858; 2018-05-31: 960; 2018-08-27: 726 |  | 816 |  | 984 | 960 | 1055 | Exhaust-Nano lab- RTP/ICPCD | 915 | Exhaust-Nano lab- RTP/ICPCD | 902.7 |  | 1251 | Exhaust-Nano lab- RTP/ICPCD | 915.7 | Exhaust-Nano lab- RTP/ICPCD | 931.1 | 831.9 |  | 815 | 831.2 |  | 785.8 |  | 667 |  | 605.5 |  | 545.1 |  | 501.6 |  | 520.9
d | AMAT Lab Etch Scrubber Exhaust |  | 6" @ outlet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2016-09-01: 434; 2017-06-21: 2245; 2017-08-17: 1321; 2018-05-31: 2675; 2018-08-27: 751 |  | 1476 |  | 1488 | 1370 | 1354 | Exhaust- AMAT lab- Etch scrubber | 2398 | Exhaust- AMAT lab- Etch scrubber | 2376 |  | 1782 | Exhaust- AMAT lab- Etch scrubber | 2287 | Exhaust- AMAT lab- Etch scrubber | 2174 | 2292 |  | 2153 | 1686 |  | 2736 |  | 2501 |  | 2390 |  | 2045 |  | 2245 |  | 2471
[5 empty] | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
3 | AMAT & NANO LABS UPS ROOM |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
a | NANO LAB 200 KVA UPS Cabinet Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2018-08-27: 3596 | [9 empty] | 358 | [8 empty] | 2253 | 1182 |  | 1724 |  | 127.1 |  | 1550 |  | 1040 |  | 1680
b | AMAT LAB 300 KVA UPS Cabinet Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2018-08-27: 0 | OFF | 452 |  |  |  |  | Exhaust-Nano lab- ups 200KVA |  | Exhaust-Nano lab- ups 200KVA | 0 | OFF |  | Exhaust-Nano lab- ups 200KVA | 582.4 | Exhaust-Nano lab- ups 200KVA | 1827 | 582.4 |  |  |  |  | 1080 |  | 1384 |  | 1028 |  | 740 |  | 1400
[5 empty] | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 | [11 empty] | 468 |  |  |  |  | Exhaust-AMAT lab- ups 300KVA |  | Exhaust-AMAT lab- ups 300KVA |  |  |  | Exhaust-AMAT lab- ups 300KVA | 0 | Exhaust-AMAT lab- ups 300KVA | 0 | 0
4 | Micro 1 Chemistry Room |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
a | Micro 1 Chemistry Room GPWB Exhaust |  | 6" @ outlet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2017-06-21: 4727; 2017-08-31: 3146; 2018-05-31: 1500; 2018-08-27: 3785 |  | 3678 |  | 3253 | 2712 | 3669 | Exhaust- Micro 1 chemistry room- GPWB | 901 | Exhaust- Micro 1 chemistry room- GPWB | 0 | OFF |  | Exhaust- Micro 1 chemistry room- GPWB | 0 | Exhaust- Micro 1 chemistry room- GPWB | 0 | 0 | [12 empty] | 0 | OFF | 0 | OFF
b | Micro 1 Chemistry Room Wet Bench Exhaust |  | 6" @ outlet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2017-06-21: 5251; 2017-08-31: 4500; 2018-05-31: 503; 2018-08-27: 5716 |  | 4501 |  | 4558 | 5806 | 4235 | Exhaust- Micro 1 chemistry room- wet bench | 3002 | Exhaust- Micro 1 chemistry room- wet bench | 0 | OFF |  | Exhaust- Micro 1 chemistry room- wet bench | 0 | Exhaust- Micro 1 chemistry room- wet bench | 0 | 0 | [8 empty] | 3002 |  | 0 | OFF | 0 | OFF | 0 | OFF
[5 empty] | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
5 | Micro 1 Yellow Room |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
a | STSRIE Exhaust | These 3 systems share a common exhaust | 6" @ outlet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL starter of these 3 systems is in Micro 1 LAB |  | 100 |  | 2017-06-21: 508; 2017-08-31: 503; 2018-05-31: 2204; 2018-08-27: 795 | Balancing of blower impeller is required | [6 empty] | 80
b | Oven Exhaust |  | 6" @ outlet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 | [11 empty] | 301 |  |  |  |  | Exhaust-Micro 1 Yellow room- STSRIE/oven/spinner |  | Exhaust-Micro 1 Yellow room- STSRIE/oven/spinner | 305 | STSRIE | 363.8 | Exhaust-Micro 1 Yellow room- STSRIE/oven/spinner | 225.7 | Exhaust-Micro 1 Yellow room- STSRIE/oven/spinner | 200.1 | 192.6 |  | 171.3 | 133.5 |  | 154.4 |  | 222.5 |  | 112.8 |  | 0 | Blower kept OFF due to noise issue | 0 | Blower kept OFF due to noise issue | 0 | Blower kept OFF due to noise issue
c | Spinner Exhaust |  | 6" @ outlet [Int. Dia] |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
[5 empty] | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
6 | Micro 1 LAB Common Exhaust | For Oxidation & FGA Furnaces |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL Starter is in Micro 1 LAB & Labelled "Furnace Exhaust" |  | 100 |  | 2017-06-21: 624; 2017-08-31: 192; 2018-05-31: 309; 2018-08-27: 173 |  | 320 |  |  |  | 551 | Exhuast- Micro 1- furnaces | 185 | Exhuast- Micro 1- furnaces | 725 |  | 165 | Exhuast- Micro 1- furnaces | 540 | Exhuast- Micro 1- furnaces | 538.6 | 505.5 |  | 448.2 | 444 |  | 494 |  | 537.4 |  | 570.9 |  | 542.8 |  | 588.9 |  | 545.5
[5 empty] | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
7 | Micro 1 & 2 LABS 300 KVA UPS Cabinet Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 | [10 empty] | Cannot be taken from outside | 1730 |  | 1803 |  |  | Exhaust- Micro 1 & 2 - UPS 300KVA |  | Exhaust- Micro 1 & 2 - UPS 300KVA | 345.2 |  |  | Exhaust- Micro 1 & 2 - UPS 300KVA | 0 | Exhaust- Micro 1 & 2 - UPS 300KVA | 0 | [7 empty] | 0 | Motor winding gone bad - mcb found tripped in DB | 2350 | Motor replaced on 17/2/2020 | 2505 |  | 3017 |  | 3472
8 | Tube Washer Exhaust - M1 YR AHU Plant Room / Old Sterlin LN2 Room |  | 8"/200 mm @ outlet |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL Starter of this system's exhaust is in Micro 1 LAB |  | 100 |  | 2018-08-27: 0 | OFF | x | Disconnected |  |  |  | Exhaust-char 2 lab- tube washer |  | Exhaust-char 2 lab- tube washer | 3153 |  |  | Exhaust-char 2 lab- tube washer | 0 | Exhaust-char 2 lab- tube washer | 0
[5 empty] | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
9 | Micro 2 LAB Common Exhaust | For HWCVD, PIII & Micro 2 LAB Toxic Gas Cabinet | 4" @ Toxic Gas Cabinet in M-2 Lab Service Corridor |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL Starter is next to Control Panel of Micro 2 LAB Chiller |  | 100 |  | 2017-08-31: 650.1 | Cannot be taken from outside | 562 |  | 572 |  |  | Exhaust- Micro 2 lab- HWCVD/PIII/ Gas cabinet |  | Exhaust- Micro 2 lab- HWCVD/PIII/ Gas cabinet | 1061 |  |  | Exhaust- Micro 2 lab- HWCVD/PIII/ Gas cabinet |  | Exhaust- Micro 2 lab- HWCVD/PIII/ Gas cabinet | 841.9 | 918 |  |  | 280.8 |  | 760 | Reading taken @ Toxic Gas Cabinet | 295 |  | 673.9 | Exhaust Blower Outlet Side | 356.5 | Toxic Gas Cabinet Side | 785 | Exhaust Blower Outlet Side | 808.8
[5 empty] | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
10 | Wet Chemistry Room Common Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 | [11 empty] | x | Lab not functioning |  |  |  | Exhaust- Biomems lab- furnaces/oven |  | Exhaust- Biomems lab- furnaces/oven | 100.8/160.8/556.7 | Wet Chemistry Room |  | Exhaust- Biomems lab- furnaces/oven | 0 | Exhaust- Biomems lab- furnaces/oven | 0 | 0 | bar: 2017-08-31
11 | N2 Plant Room Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
a | N2 Plant Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2017-07-07: 3506; 2017-08-31: 3805; 2018-05-31: 3430; 2018-08-27: 3679 |  | 3570 |  |  | 3114 |  | Exhaust- N2 plant | 2785 | Exhaust- N2 plant | 3568 |  |  | Exhaust- N2 plant |  | Exhaust- N2 plant | 1955 | 2901 |  | 2907 | 2745 |  | 3125 |  | 3546 |  | 2947 |  | 3050 |  | 2341 |  | 1603
b | N2 Plant Standby Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2018-05-31: 2153; 2018-08-27: 2116 |  | 1175 |  |  | 1090 |  |  | 1204 |  | 2222 | [5 empty] | 1035 | 1020 |  | 1051 | 600.9 |  | 0 | Motor needs to be changed - winding gone bad | 0 | Motor needs to be changed - winding gone bad | 1007 | Motor was replaced on 17 Dec 2020 | 1050 |  | 1039 |  | 1274
c | N2 Plant Exhaust Blower @ EE Annex Bldg Terrace | [35 empty] | 3153 | 3322 |  | 2030 |  | 2050 |  | 2901 |  | 2793 |  | 2141 |  | 3008
12 | New Building UPS Room |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 | [23 empty] | 3223 | New Exhaust - N2 Plant [9691 CFM] | 3137 | 2385
a | New Building 300 KVA UPS (Ground & First Floor) - Cabinet Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL Starter is in N2 Plant Room |  | 100 |  | 2017-07-07: 3405; 2017-08-31: 100; 2018-05-31: 3306; 2018-08-27: 3401 |  | 3568 |  | 7161 |  |  | Exhaust- New Bldg Gr & 1st floor-UPS 300KVA |  | Exhaust- New Bldg Gr & 1st floor-UPS 300KVA | 3054 |  |  | Exhaust- New Bldg Gr & 1st floor-UPS 300KVA | 3045 | Exhaust- New Bldg Gr & 1st floor-UPS 300KVA | 2747 | 895 |  |  | 2316 |  | 3528 | Blower made up on 16/8/2020 after motor changed due to winding gone bad | 3648 |  | 645.5 | Taken @ UPS Cabinet Exhaust Side | 2150 | Taken @ E.B. Outlet Side | 1815 | Taken @ E.B. Outlet Side | 1404
b | New Building 300 KVA UPS (2nd, 3rd & 5th Floor) - Cabinet Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL Starter is in N2 Plant Room |  | 100 |  | 2017-07-07: 3362; 2017-08-31: 2664; 2018-05-31: 3568; 2018-08-27: 3114 |  | 3584 |  | 4521 |  |  | Exhaust- New Bldg 2nd, 3rd & 5th floor-UPS 300KVA |  | Exhaust- New Bldg 2nd, 3rd & 5th floor-UPS 300KVA | 1643 |  |  | Exhaust- New Bldg 2nd, 3rd & 5th floor-UPS 300KVA | 1583 | Exhaust- New Bldg 2nd, 3rd & 5th floor-UPS 300KVA | 1689 | 354.6 |  |  | 1650 |  | 1643 |  | 1747 |  | 610 | Taken @ UPS Cabinet Exhaust Side | 1403 | Taken @ E.B. Outlet Side | 1183 | Taken @ E.B. Outlet Side | 1202
13 | New Building MBE LAB Service Corridor |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 | [17 empty] | 1442
| MBE LAB 0.2 Instrument Exhaust |  | 8"/200 mm @ inlet to Exhaust Blower |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2017-06-21: 1320 |  |  |  |  | 2175 |  | Exhaust- MBE lab- flip chip |  | Exhaust- MBE lab- flip chip | 763 |  |  | Exhaust- MBE lab- flip chip | 2684 | Exhaust- MBE lab- flip chip | 2215 | 2305 |  | 1035 | 1732 |  | 1035 |  | 1609 |  | 1206 |  | 1507 |  | 2053 |  | 1875
[5 empty] | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
14 | New Building 1st Floor Labs Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
a | General Purpose Wet Bench 1.2 LAB |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL Starter is in 1.2 LAB |  | 100 |  | 2016-09-01: 163.5 & 158.5 | [6 empty] | Exhaust- New bldg 1st floor- GPWB |  | Exhaust- New bldg 1st floor- GPWB | 212 |  |  | Exhaust- New bldg 1st floor- GPWB |  | Exhaust- New bldg 1st floor- GPWB
b | Lasers 1 & 2 in 1.2 LAB & New Toxic Gas Cabinet |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL Starter is in 1.2 LAB |  | 100 | [16 empty] | Exhaust- New bldg 1st floor- laser/PLD |  | Exhaust- New bldg 1st floor- laser/PLD | 2670 |  |  | Exhaust- New bldg 1st floor- laser/PLD |  | Exhaust- New bldg 1st floor- laser/PLD
c | Toxic Gas Cabinet, Scrubber of ICPRIE & NCPRE Edge Isolation Tool |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL Starter is in Service Corridor of 1.1 & 1.2 LABS |  | 100 |  | 2016-09-01: 2207; 2017-06-21: 851; 2017-08-31: 245; 2018-05-31: 204/102; 2018-08-27: 1401; 141 | 1401 FPM in Gas Cabinet Outlet & 141 FPM in Scrubber Outlet | 862 |  |  | 1705 | 858 | Exhaust-New bldg 1st floor- RIE/gas cabinet/ scrubber | 1486 | Exhaust-New bldg 1st floor- RIE/gas cabinet/ scrubber | 858 |  |  | Exhaust-New bldg 1st floor- RIE/gas cabinet/ scrubber | 868 | Exhaust-New bldg 1st floor- RIE/gas cabinet/ scrubber | 200.9 | 187 |  |  | 130.6 | Damper 10% Open | 280.4 | Damper 20% Open | 280 |  | 175.2 |  | 145.6 |  | 230.6 |  | 225
d | Edwards GRC M150 Toxic Gas Scrubber Cabinet Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 | [19 empty] | 1503 |  |  |  | 380.7 |  | 0 | [7 empty] | 2158 |  | 1707 |  | 1478 |  | 1287 |  | 1800
e | New Toxic Gas Cabinet for PDS Toxic Gas Cylinders | [30 empty] | 1165 |  | 4955 | 3562 |  |  | 4709 |  | 2707 |  | 1324 |  | 878.8 |  | 4656 |  | 3540 |  | 1687
15 | New Building 2nd Floor NCPRE LAB Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
a | NCPRE RCA Wet Bench Exhaust |  | 10" @ intake to Exhaust Blower |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL Starter is in NCPRE 2.2 LAB |  | 100 |  | 2016-09-01: 91.5 | [6 empty] | Exhaust- NCPRE lab- RCA wet bench |  | Exhaust- NCPRE lab- RCA wet bench | 237 |  |  | Exhaust- NCPRE lab- RCA wet bench |  | Exhaust- NCPRE lab- RCA wet bench
b | NCPRE Etching/Texturing Wet Bench Exhaust |  | 10" @ intake to Exhaust Blower |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL Starter is in NCPRE 2.2 LAB |  | 100 |  | 2016-09-01: 144 | [6 empty] | Exhuast- NCPRE lab- etching/texturing wet bench |  | Exhuast- NCPRE lab- etching/texturing wet bench | 0 | Wet Bench System is OFF |  | Exhuast- NCPRE lab- etching/texturing wet bench |  | Exhuast- NCPRE lab- etching/texturing wet bench
c | NCPRE Toxic Gas Cabinet, RTP, New PECVD, Pro Temp Furnace Exhaust |  | 6" @ Toxic Gas Cabinet Outlet |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL Starter is in Service Corridor of 2.1 & 2.2 NCPRE LAB |  | 100 |  | 2016-09-01: 2070; 2017-08-31: 768 |  |  |  | 2273 |  |  | Exhaust- NCPRE lab- Gas cabinet/ RTP/New PECVD/ protemp |  | Exhaust- NCPRE lab- Gas cabinet/ RTP/New PECVD/ protemp | 2639 | 3820 FPM measured inside @ Pro Temp Furnace System Exhaust Outlet inside 2.2 Lab |  | Exhaust- NCPRE lab- Gas cabinet/ RTP/New PECVD/ protemp | 2050 | Exhaust- NCPRE lab- Gas cabinet/ RTP/New PECVD/ protemp | 2434 | [5 empty] | 1907 |  | 2413 |  | 670.8 |  | 1904 |  | 2091 |  | 1955
d | NCPRE Scrubber, Old PECVD, Three Stack Furnace, Spray Coater, Hot Air Oven Exhaust |  | 6" @ Toxic Gas Cabinet Outlet & 8" @ intake to Exhaust Blower; |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L | DOL Starter is in Service Corridor of 2.1 & 2.2 NCPRE LAB |  | 100 |  | 2016-09-01: 495 |  |  |  | 1868 |  |  | Exhuast- NCPRE lab- Scrubber/ old PECVD/ 3 stack furnace/ spray coater/ hot air oven |  | Exhuast- NCPRE lab- Scrubber/ old PECVD/ 3 stack furnace/ spray coater/ hot air oven | 1446 |  |  | Exhuast- NCPRE lab- Scrubber/ old PECVD/ 3 stack furnace/ spray coater/ hot air oven | 526.7 | Exhuast- NCPRE lab- Scrubber/ old PECVD/ 3 stack furnace/ spray coater/ hot air oven | 888.8 | [7 empty] | 654.7 |  | 525.9 |  | 547 |  | 510.5 |  | 468.1
e | NCPRE New Toxic Gas Cabinet |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 | [23 empty] | 1295 |  | 1470 | [5 empty] | 1470 |  | 1304 |  | 1004 |  | 1098 |  | 1358 |  | 1262
16 | EC LAB Exhaust |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
a | General Purpose Wet Bench | All systems share a common exhaust |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2017-08-31: 365; 2018-05-31: 673 |  | 669 |  |  | 431 |  | Exhaust-EC lab- GPWB |  | Exhaust-EC lab- GPWB | 465.5 |  |  | Exhaust-EC lab- GPWB | 784.2 | Exhaust-EC lab- GPWB | 876.5 | 1310 |  |  | 1039 |  | 1053 |  | 974.2 |  | 1028 |  | 1952 |  | 750 |  | 1080
b | Gold Electro-Plating System | All systems share a common exhaust |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2017-08-31: 306; 2018-05-31: 673 |  | 372 |  |  | 214 |  | Exhaust-EC lab- electroplating |  | Exhaust-EC lab- electroplating | 321 |  |  | Exhaust-EC lab- electroplating |  | Exhaust-EC lab- electroplating
c | Oven 1 | All systems share a common exhaust |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
d | Oven 2 | All systems share a common exhaust |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 | [23 empty] | 784.2
17 | New Building 7th Floor - Biosensor lab |  |  |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100
a | laser engraving system |  | 2" @ system end |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2016-09-01: 6607; 2017-06-21: 235; 2017-08-31: 0 |  | x | Process going on | [6 empty] | 0 | SYSTEM IS OFF |  |  | 106 |  | 105 |  | Wet Bench is off |  | 142/145.7 |  | 173/104 |  | 117.5 |  | 0 | Exhaust Outlet Blocked with Cello-Tape inside the System/Tool | 1475 |  | 146.1 |  | 224.7
b | wet bench |  | 10" @ intake to Exhaust Blower |  | Hindustan Electric; 3 Ph; 415 V/50Hz/1.5 KW/2.0 HP/3.3 Amps/Duty S1/IP 55/Insulation Class F/Frame 90L |  |  | 100 |  | 2016-09-01: 1463 & 2153; 2017-06-21: 138 (L) / 175 (R); 2017-08-31: 132.2 LHS / 166 RHS |  | 590 |  | 503 |  | 421 |  | 357 |  | 106.4 (LHS) / 147.6 (RHS) |  |  |  | 132.8/142.9 |  | 464.4/429 |  | Laser Engraver is off |  | 0 | Kept off due to dead bird [parrot] found in exhaust line; Remedy: Put Jaali @ Exhaust Blower outlet on New Bldg Terrace to prevent a repeat of this insident. Plan to cover all EB outlets with jaali in Short Term. | 190.4 |  | 150.1 |  | 119.4/167.1 |  | 146.5/155.8 |  | 94.4/170.9 |  | 95.3/170.5
18 | New Building 7th Floor - 7.1 Amat Clean Lab
a | Fume Hood 1 | [26 empty] | 176 |  |  |  | 175 |  | 160.6 | 215.4 |  |  | 184 | Fume Hood Side | 216.8 |  | 90.1 |  | 225.4 |  | 195.5 |  | 175.2 |  | 185.5
b | Fume Hood 2 | [26 empty] | 0 | Impeller Issue / Motor makes noise in running condition hence kept OFF |  |  | 125.3 |  | 90.9 | 0 | Fume Hood is OFF |  | 95.1 | Fume Hood Side | 165 |  | 95.6 |  | 155.2 |  | 141.9 |  | 140.6 |  | 144.1
c | Fume Hood 3 | [26 empty] | 174 |  |  |  | 150 |  | 80 | 0 | Fume Hood is OFF |  | 190.7 | Fume Hood Side | 181 |  | 184.2 |  | 215.5 |  | 134.8 |  | 153.6 |  | 208.4
d | Fume Hood 4 | [26 empty] | 120 |  |  |  | 0 |  | 176 | 0 | Fume Hood is OFF |  | 184 | Fume Hood Side | 165 |  | 129 |  | 230.9 |  | 207.5 |  | 218.9 |  | 169.5
e | Fume Hood 5 | [26 empty] | 164.6 |  |  |  | 140.3 |  | 131.6 | 146 |  |  | 158 | Fume Hood Side | 173.6 |  | 160 |  | 128.6 |  | 173.5 |  | 184.5 |  | 195.6
f | Common Exhaust for Furnace & Vapour Generator System | [30 empty] | 2185 |  | 2195
19 | Organic Electronics / HSC [NCPRE] Lab - 1st Floor EE Annex Bldg
| Wet Bench | [26 empty] | 850 (LHS) / 800 (RHS) | 167 @ Work Area |  |  | 2204 |  | 2250 | [7 empty] | 2416 |  | 2571 |  | 0 | OFF |  | OFF |  | OFF
20 | Char 2 Lab - Facility Exhaust | [36 empty] | 213.6 | Made Functional On 29/2/2020 for Planar Tech CVD Set Up | 199 |  | 228.2 |  | 163.7 |  | 190.7 |  |  | OFF | 225.9
21 | Wet Chemistry Room Exhaust
22 | Chemical Storage Room Exhaust | [38 empty] | 407.3 |  | 265.4 | [7 empty] | 185.6
Legend
Colour | Area Description | ZONE NO.
| EE Annex Building Side of IITBNF Complex | 1
| N2 Plant Room & New N2 Shed & Platform Area of IITBNF Complex | 2
| New Nano - Electronics Building Side of IITBNF Complex | 3