## Summary Sheet
UPS | 2017-07-01 | 2017-08-01 | 2017-09-01 | 2017-10-01 | 2017-11-01 | 2017-12-01 | 2018-01-01 | 2018-02-01 | Comments | 2018-03-01 | Comments | 2018-07-01 | Comments | 2018-08-08 | Comments | 24-10-2018 | Comments | 21-1-2019 | Comments | 27/8/2019 | Comments | 27/9/2019 | Comments | 2019-04-10 | Comments | 31/10/2019 | Comments | 26/11/2019 | Comments | 2020-11-12 | Comments | 2021-05-05 | Comments
AMAT | 2 | 2 |  |  | 5 |  | 4 |  | Only Failed Batteries Considered. Not Changed |  |  |  | To Be Checked |  | To Be Checked |  |  |  | Many Batteries reading not even coming |  | Many reading not coming. UPS not in use |  | Not Taken. UPS not in use. |  |  |  | Not Taken. UPS not in use. |  | Not Taken. UPS not in use. |  | Not Taken. UPS not in use. |  | Not Taken. UPS not in use.
NANO |  | 4 | [6 empty] | Only 5 "Warning" Batteries were replaced in Jan 2018 | 26/3/2018 | 32 new batteries installed on the second battery bank and old batteries removed. | 0 | All Pass |  | To Be Checked |  |  | 64 | All Pass | 64 | All Pass | 1 | 1 Battery showing Failed |  |  | 64 | All Pass | 64 | All Pass | 64 | All Pass | 64 | All Pass
M1/M2 | [11 empty] | 16 | In Warning Stage |  | To Be Checked |  |  | 83 | 5 Batteries showing Failed & 78 Batteries showing Warning | 5 | 3 Warning & 2 Failed , Remaining 115 Passed. Battery Bank was fully changed on 3&4 August 2019 | 8 | 8 Batteries showing Failed |  |  | 9 | 4 Batteries showing Warning & 5 Batteries showing Failed | 15 | 2 Batteries showing Warning & 13 Batteries showing Failed | 27 | 2 Batteries showing Warning & 25 Batteries showing Failed |  | Need to be taken
MBE | 2 |  |  | 0 | 1 |  |  |  | 2 Batteries replace in October. 1 required to be changed as no reading is coming. |  |  |  | To Be Checked | 0 | All Pass |  |  | 3 | 2 Showing Failed & Battery reading did not come | 1 | 1 Battery reading did not come. Rest are Passed. | 1 | 1 Battery reading did not come. Rest are Passed. |  |  | 2 | 1 Battery showing Warning & 1 Battery reading did not come | 1 | 1 Battery showing Failed | 58 | 34 Batteries showing Warning & 24 Batteries showing Failed | 80
NCPRE |  |  |  |  | 1 |  | 0 |  | Replaced on 2/2/2018 |  |  |  | To Be Checked | 0 | All Pass |  |  | 1 | 1 Battery reading did not come | 120 | All Pass | 1 | 1 Battery reading did not come |  |  | 1 | 1 Battery showing Warning | 1 | 1 Battery showing Warning | 14 | 8 Batteries showing Warning & 6 Batteries showing Failed | 21
NMPF | [23 empty] | 44 | All Pass
AL & PC CELL MBE LAB LAHA SIR 10 KVA UPS
GAL 6 SC SIR MBE LAB 10 KVA UPS
GAL EURO MBE LAB LAHA SIR 10 KVA UPS
EC Lab 10 KVA UPS
MCL UPS 1 15 KVA
MCL UPS 2 15 KVA
IT Team Office 6 KVA UPS
Micro 2 Lab XPS 10 KVA UPS
HSC [OE] [NCPRE] Lab UPS - Newly Added

## Reference Sheet
Battery Internal Resistance [IR] Specs by Voltage & AH [Ampere Hours]
Sr. No. | Voltage | AH | Max IR (m-ohm)
1 | 12 | 7 | 22
2 | 12 | 9 | 18
3 | 12 | 12 | 16
4 | 12 | 17 | 15
5 | 12 | 26 | 10
6 | 12 | 42 | 8
7 | 12 | 65 | 8
8 | 12 | 75 | 8
9 | 12 | 100 | 6
10 | 12 | 120 | 6
11 | 12 | 150 | 6
12 | 12 | 200 | 5
LEGEND/KEY
Pass | Below 1.5 x Max IR
Warning | Between 1.5 x Max IR to 2.0 x Max IR
Fail | Above 2.0 x Max IR

## AMAT
Battery Spec: 12 Volts 120 AH
Brand: Exide Powersafe
Sr. No. | 2017-07-21 | 31/8/2017 | 15/11/2017 | 2018-10-01 | Comments - 10/1/2017
1 | 4.5 | 6.1 | 6.4 | 4.9 | PASS
2 | 4.4 | 4.6 | 4.5 | 4.6 | PASS
3 | 4.2 | 4.3 | 9999 | OF. | 5.6 came as reading in 2nd attempt - PASS
4 | 3.9 | 3.9 | 3.8 | 4 | PASS
5 | 12.5 | 30 | 77.6 | 24.5 | FAIL
6 | 5.7 | 5.5 | 5.2 | 4.1 | PASS
7 | 3.4 | 3.6 | 3.8 | 4.8 | PASS
8 | 4.5 | 5.1 | 5.1 | 4.3 | PASS
9 | 4.6 | 5.2 | 5 | 4.9 | PASS
10 | 5 | 5.1 | 4.5 | 3.9 | PASS
11 | 4.6 | 5.4 | 4.5 | 5.3 | PASS
12 | 3.7 | 3.8 | 3.9 | 4.6 | PASS
13 | 5.6 | 5.4 | 5.7 | 3.8 | PASS
14 | 5.4 | 5.2 | 4.8 | 4.7 | PASS
15 | 5.1 | 4.8 | 4.8 | 5.2 | PASS
16 | 5 | 5.7 | 5.7 | 5.3 | PASS
17 | 5.7 | 5.9 | 6.5 | 5 | PASS
18 | 6.8 | 6 | 6.5 | 3.7 | PASS
19 | 5.1 | 3.8 | 3.9 | 4.8 | PASS
20 | 3.7 | 5.9 | 7.1 | 5.2 | PASS
21 | 5.4 | 5.5 | 6.2 | 5.2 | PASS
22 | 5 | 5.3 | 6.7 | 4.8 | PASS
23 | 4.8 | 6.5 | 10.9 | 4.9 | PASS
24 | 5.9 | 3.6 | 3.8 | 69.7 | FAIL
25 | 5.3 | 118.3 | 43.3 | 3.6 | PASS
26 | 3.8 | 6.3 | 6.7 | 127.4 | FAIL
27 | 125.9 | 5.2 | 4.6 | 10 | PASS
28 | 4.9 | 6.4 | 4.6 | 5.5 | PASS
29 | 4.5 | 6.2 | 5.4 | 5.1 | PASS
30 | 4.4 | 5.6 | 8.8 | 4.7 | PASS
31 | 5.1 | 4.5 | 5.5 | 5.4 | PASS
32 | 4.6 | 5.4 | 4.5 | 5.3 | PASS
33 | 5.8 | 4.1 | 3.9 | 4.5 | PASS
34 | 7 | 3.8 | 3.8 | 4.3 | PASS
35 | 5 | 4.8 | 4.9 | 4.1 | PASS
36 | 4.5 | 7.6 | 8.3 | 5.3 | PASS
37 | 4.6 | 5.7 | 5.4 | 9.3 | PASS
38 | 5 | 6.7 | 4.6 | 8.1 | PASS
39 | 5.7 | 6.1 | 4.9 | 4.8 | PASS
40 | 8.2 | 5.2 | 5.2 | 5 | PASS
41 | 3.9 | 5.6 | 4.9 | 5 | PASS
42 | 5.6 | 7.9 | 6.7 | 5.5 | PASS
43 | 6.4 | 3.8 | 3.5 | 5.5 | PASS
44 | 6.9 | 7.3 | 6.2 | 5.2 | PASS
45 | 5.9 | 5.5 | 6 | 7.9 | PASS
46 | 7.9 | 7.2 | 6.5 | 3.7 | PASS
47 | 4.1 | 5.7 | 5.7 | 7.3 | PASS
48 | 5.8 | 5.6 | 5.5 | 7.2 | PASS
49 | 5.8 | 3.6 | 3.9 | 6.3 | PASS
50 | 6.6 | 6.1 | 5.7 | 3.9 | PASS
51 | 6.4 | 6.8 | 6.1 | 6.2 | PASS
52 | 6.8 | 5.6 | 5 | 6.4 | PASS
53 | 3.7 | 6.8 | 6.6 | 7.4 | PASS
54 | 6.3 | 3.7 | 3.7 | 4 | PASS
55 | 3.6 | 6.5 | 5.9 | 10.2 | WARNING
56 | 6.8 | 3.6 | 3.7 | 3.6 | PASS
57 | 3.8 | 7.9 | 7.5 | 9.6 | PASS
58 | 8.3 | 3.8 | 3.7 | 3.5 | PASS
59 | 3.9 | 8.3 | 8.7 | 6.6 | PASS
60 | 4.4 | 3.8 | 4 | 3.7 | PASS
61 | 4.2 | 5.3 | 5.3 | 7.9 | PASS
62 | 4.5 | 4.8 | 4.2 | 5.2 | PASS
63 | 4.7 | 5.3 | 4.6 | 7.8 | PASS
64 | 4.3 | 4.9 | 4.9 | 4.4 | PASS
65 | 4.5 | 4.9 | 4.4 | 4.2 | PASS
66 | 4.2 | 5.6 | 5.6 | 4.7 | PASS
67 | 4.1 | 4.7 | 4.5 | 5 | PASS
68 | 10.4 | 4.6 | 6.1 | 4.5 | PASS
69 | 4.4 | 6.1 | 11.1 | 5.5 | PASS
70 | 4 | 4.8 | 4.6 | 5 | PASS
71 | 4.4 | 4 | 3.6 | 4.7 | PASS
72 | 4.4 | 5.7 | 4.5 | 71.2 | FAIL
73 | 7.6 | 4.8 | 4.6 | 5.9 | PASS
74 | 5.2 | 11.1 | 9999 | 3.9 | PASS
75 | 4.4 | 5.1 | 5 | 5.7 | PASS
76 | 4.5 | 5.2 | 4.7 | 6.5 | PASS
77 | 4.6 | 4.4 | 4.8 | OF. | 4.9 came as reading in 2nd attempt - PASS
78 | 5.2 | 5.8 | 4.5 | 5.9 | PASS
79 | 4.2 | 3.9 | 4 | 4.8 | PASS
80 | 6.1 | 6.2 | 4.8 | 3.7 | PASS
81 | 4.2 | 3.9 | 4.1 | 4.5 | PASS
82 | 6.5 | 5.7 | 4.5 | 4.8 | PASS
83 | 5.2 | 5.5 | 4.6 | 4.8 | PASS
84 | 4.8 | 5.1 | 4.3 | 3.6 | PASS
85 | 4.1 | 3.8 | 4 | 4.5 | PASS
86 | 4.9 | 6.4 | 5.4 | 4.7 | PASS
87 | 6.1 | 5.4 | 4.7 | 4.4 | PASS
88 | 5 | 5.1 | 4.2 | 3.9 | PASS
89 | 4.6 | 5.4 | 4.8 | 5.2 | PASS
90 | 4.1 | 5.8 | 5.6 | 4.9 | PASS
91 | 4.9 | 4.9 | 5.3 | 4.2 | PASS
92 | 5 | 5 | 4.6 | 4.7 | PASS
93 | 3.8 | 4.3 | 3.8 | 4.9 | PASS
94 | 4.8 | 5.3 | 3.6 | 5 | PASS
95 | 4.3 | 6.2 | 4.4 | 4.7 | PASS
96 | 5.3 | 7 | 4.7 | 3.9 | PASS
97 | 5.3 | 6 | 6.1 | 3.6 | PASS
98 | 5.5 | 5.7 | 5.2 | 4.5 | PASS
99 | 4.3 | 5.1 | 4.5 | 3.6 | PASS
100 | 4.3 | 5.5 | 3.6 | 4.6 | PASS
101 | 4.9 | 5 | 4.7 | 5.2 | PASS
102 | 3.7 | 6.5 | 3.7 | 6.2 | PASS
103 | 5.6 | 6.5 | 6 | 4.9 | PASS
104 | 5 | 6.3 | 5.3 | 4.9 | PASS
105 | 5.6 | 5.4 | 5.3 | 3.6 | PASS
106 | 4.6 | 5.6 | 4.1 | 7.1 | PASS
107 | 4.5 | 6.7 | 4.2 | 6.6 | PASS
108 | 6.4 | 5.6 | 5.2 | 6.7 | PASS
109 | 4.2 | 7.3 | 4.6 | 5.7 | PASS
110 | 4.3 | 4.9 | 4.5 | 5.7 | PASS
111 | 4.8 | 6.6 | 4.2 | 5.7 | PASS
112 | 6.6 | 5.5 | 4.4 | 4.6 | PASS
113 | 5.2 | 3.7 | 4.4 | 4.6 | PASS
114 | 3.8 | 5.5 | 3.8 | 4.6 | PASS
115 | 5.3 | 4.1 | 5.8 | 5.7 | PASS
116 | 4.1 | 6.3 | 4 | 4.4 | PASS
117 | 5.8 | 6.7 | 4.5 | 4.5 | PASS
118 | 6.2 | 6 | 63.8 | 4.2 | PASS
119 | 5.7 | 6 | 5.2 | 4.5 | PASS
120 | 5.4 | 5.9 | 4.5 | 4.6 | PASS

## NANO
Battery Spec: 12 Volts 150 AH
Brand: Exide Powersafe
Sr.No. | 2017-07-21 | 30/8/2017 | 15/11/2017 | 20/12/2017 | Comments - 20/12/2018 | 2018-10-01 | Comments - 10/1/2018 | 2018-11-01 | Comments - 11/1/2018 | 2018-09-02 | Comments - 9/2/2018 | New Battery Reading | 19/2/2018 | Comments - 19/2/2018 | 26/3/2018 | Comments - 26/3/2018 | 2018-03-07 | Comments - 3/7/2018 | 24/10/2018 | Comments - 24/10/2018 | 21/1/2019 | Comments - 21/1/2019 | 19/8/2019 | Comments - 19/8/2019 | 27/9/2019 | Comments - 27/9/2019 | 31/10/2019 | Comments - 31/10/2019 | 26/11/2019 | Comments - 26/11/2019 | 2020-09-01 | Comments - 9/1/2020 | 25/2/2020 | Comments - 25/2/2020 | 2020-07-12 | Comments - 7/12/2020 | 25/1/2021 | Comments - 25/1/2021 | 2021-09-03 | Comments - 9/3/2021 | 27/4/2021 | Comments - 27/4/2021
1 | 7.3 | 8.7 | 3.2 | 2.4 | PASS | 3.7 | Pass |  |  | 3 |  |  | 3.3 |  |  |  | 3 | Pass | 2.9 | Pass | 2.7 | Pass | 3.1 | Pass | 2.8 | Pass | 3 | Pass | 2.9 | Pass | 5.52 | Pass | 2.93 | Pass | 3.05 | Pass | 3.26 | Pass | 3.26 | Pass | 3.6 | Pass
2 | 4.9 | 9.1 | 3.2 | 3.1 | PASS | 3.1 | Pass |  |  | 3.2 |  |  | 3 |  |  |  | 3.9 | Pass | 3.1 | Pass | 3 | Pass | 2.7 | Pass | 3.3 | Pass | 3.2 | Pass | 2.8 | Pass | 6.56 | Pass | 3.63 | Pass | 3.33 | Pass | 3.27 | Pass | 3.4 | Pass | 4.2 | Pass
3 | 2.5 | 2.7 | 3.5 | 3.1 | PASS | 3.3 | Pass |  |  | 3.3 |  |  | 3.7 |  |  |  | 3.2 | Pass | 3.3 | Pass | 3.2 | Pass | 3.3 | Pass | 3.7 | Pass | 3.2 | Pass | 2.5 | Pass | 5.74 | Pass | 3.34 | Pass | 3.36 | Pass | 3.38 | Pass | 3.43 | Pass | 3.2 | Pass
4 | 6.2 | 7.1 | 7.1 | 6.6 | PASS | 8.6 | Pass |  |  | 9 | Replaced during Nano AHU & Chiller PM | 2.3 | 3.1 |  |  |  | 2.9 | Pass | 3.2 | Pass | 3.7 | Pass | 2.7 | Pass | 3.5 | Pass | 3.4 | Pass | 3.6 | Pass | 6.8 | Pass | 3.19 | Pass | 3.45 | Pass | 3.43 | Pass | 3.51 | Pass | 3.5 | Pass
5 | 9.8 | 71.8 | 9.4 | 7.9 | PASS | 8.4 | Pass |  |  | 8.6 |  |  | 8.2 |  |  |  | 3.5 | Pass | 3.4 | Pass | 2.6 | Pass | 3.1 | Pass | 2.8 | Pass | 2.9 | Pass | 3.5 | Pass | 6.07 | Pass | 3.51 | Pass | 3.19 | Pass | 3.25 | Pass | 3.29 | Pass | 4 | Pass
6 | 7.7 | 8.2 | 7.2 | 8 | PASS | 9.7 | Warning | 2.5 | Replaced with new one | 3 |  |  | 3.3 |  |  |  | 3.5 | Pass | 3.2 | Pass | 3.3 | Pass | 3.1 | Pass | 7.5 | Pass | 3 | Pass | 3.2 | Pass |  | No Reading Came | 3.34 | Pass | 3.31 | Pass | 3.41 | Pass | 3.48 | Pass | 2.5 | Pass
7 | 7.2 | 6.8 | 6.9 | 7.4 | PASS | 10.5 | Warning | 2.8 | Replaced with new one | 2.8 |  |  | 3.2 |  |  |  | 2.8 | Pass | 2.9 | Pass | 3 | Pass | 3 | Pass | 2.9 | Pass | 3.2 | Pass | 2.7 | Pass | 5.25 | Pass | 2.97 | Pass | 3.13 | Pass | 3.25 | Pass | 3.23 | Pass | 3.4 | Pass
8 | 5.8 | 10 | 9.6 | 9.7 | WARNING | 2.9 | Pass |  |  | 3.1 |  |  | 3.2 |  |  |  | 3.9 | Pass | 2.6 | Pass | 2.6 | Pass | 3.4 | Pass | 3.2 | Pass | 3.2 | Pass | 3.1 | Pass | 3.09 | Pass | 3.23 | Pass | 3.24 | Pass | 3.2 | Pass | 3.22 | Pass | 3.1 | Pass
9 | 7.5 | 10.6 | 8.3 | 8.6 | PASS | 6.8 | Pass |  |  | 7.3 |  |  | 7.9 |  |  |  | 3.6 | Pass | 3.5 | Pass | 3.1 | Pass | 2.9 | Pass | 3.4 | Pass | 3.3 | Pass | 4 | Pass | 3.32 | Pass | 3.55 | Pass | 3.28 | Pass | 3.36 | Pass | 3.4 | Pass | 2.9 | Pass
10 | 8.3 | 7.9 | 3.3 | 3.3 | PASS | 8.1 | Pass |  |  | 7.5 |  |  | 7 |  |  |  | 3.3 | Pass | 3 | Pass | 3.2 | Pass | 3.3 | Pass | 3.1 | Pass | 3.2 | Pass | 3.1 | Pass | 3.11 | Pass | 3.65 | Pass | 3.22 | Pass | 3.46 | Pass | 3.43 | Pass | 3.2 | Pass
11 | 7.3 | 6.3 | 3.2 | 3.1 | PASS | 8.7 | Pass |  |  | 8.9 |  |  | 10.2 | Warning |  |  | 3.4 | Pass | 2.8 | Pass | 3 | Pass | 2.8 | Pass | 3.2 | Pass | 3.3 | Pass | 3 | Pass | 3.08 | Pass | 3.55 | Pass | 3.14 | Pass | 3.36 | Pass | 3.31 | Pass | 3.5 | Pass
12 | 5.7 | 6.7 | 3.3 | 2.6 | PASS | 3.1 | Pass |  |  | 3 |  |  | 3.2 |  |  |  | 3 | Pass | 3.3 | Pass | 3 | Pass | 2.6 | Pass | 3.2 | Pass | 3.3 | Pass | 3.1 | Pass | 3.61 | Pass | 3.09 | Pass | 3.15 | Pass | 3.25 | Pass | 3.44 | Pass | 3.6 | Pass
13 | 6 | 6 | 3 | 3.2 | PASS | 9 | Warning |  | Replacement pending | 3.7 |  |  | 3.6 |  |  |  | 3.4 | Pass | 3.6 | Pass | 2.5 | Pass | 2.7 | Pass | 3.1 | Pass | 3.1 | Pass | 2.4 | Pass | 3.16 | Pass | 3.66 | Pass | 3.3 | Pass | 3.34 | Pass | 3.33 | Pass | 3.4 | Pass
14 | 8 | 7 | 7.8 | 8.9 | PASS | 7.6 | Pass |  |  | 10.3 | Replaced during Nano AHU & Chiller PM | 2.1 | 3.4 |  |  |  | 3.1 | Pass | 3.1 | Pass | 2.9 | Pass | 3.1 | Pass | 3 | Pass | 2.9 | Pass | 2.8 | Pass | 2.79 | Pass | 2.95 | Pass | 3.15 | Pass | 3.28 | Pass | 3.15 | Pass | 3.7 | Pass
15 | 6.3 | 7.2 | 6.7 | 8.3 | PASS | 7.4 | Pass |  |  | 9.1 | Replaced during Nano AHU & Chiller PM | 2.3 | 3.4 |  |  |  | 2.7 | Pass | 3.5 | Pass | 3.1 | Pass | 2.8 | Pass | 3 | Pass | 3.4 | Pass | 3.2 | Pass | 2.84 | Pass | 3.35 | Pass | 3.27 | Pass | 3.28 | Pass | 3.38 | Pass | 2.8 | Pass
16 | 6.3 | 8.4 | 3.3 | 3.2 | PASS | 10.5 | Warning | 2.7 | Replaced with new one | 7.4 |  |  | 7.3 |  |  |  | 3.3 | Pass | 3.1 | Pass | 3.1 | Pass | 2.3 | Pass | 2.6 | Pass | 3.2 | Pass | 3.1 | Pass | 3.68 | Pass | 3.37 | Pass | 3.44 | Pass | 3.39 | Pass | 3.44 | Pass | 3.6 | Pass
17 | 6.8 | 4 | 7.4 | 8 | PASS | 9.4 | Warning |  | Replacement pending | 8.1 |  |  | 8.2 |  |  |  | 2.8 | Pass | 3.1 | Pass | 3.1 | Pass | 3.2 | Pass | 3.2 | Pass | 3.3 | Pass | 3 | Pass | 3.57 | Pass | 3.19 | Pass | 3.15 | Pass | 3.35 | Pass | 3.39 | Pass | 3.3 | Pass
18 | 3.7 | 10.9 | 9.2 | 8.5 | PASS | 3.4 | Pass |  |  | 9 |  |  | 3.1 |  |  |  | 3 | Pass | 2.8 | Pass | 3.6 | Pass | 2.9 | Pass | 3.3 | Pass | 3.2 | Pass | 3.3 | Pass | 3.56 | Pass | 2.86 | Pass | 3.14 | Pass | 3.34 | Pass | 3.3 | Pass | 3.9 | Pass
19 | 6.1 | 6.8 | 8.7 | 8 | PASS | 2.9 | Pass |  |  | 9999 |  |  | 3.2 |  |  |  | 3.3 | Pass | 3.4 | Pass | 2.9 | Pass | 3.7 | Pass | 2.9 | Pass | 3 | Pass | 2.7 | Pass | 3.34 | Pass | 3.16 | Pass | 3.12 | Pass | 3.23 | Pass | 3.29 | Pass | 3.7 | Pass
20 | 6.5 | 9.3 | 3.1 | 3.2 | PASS | 3.2 | Pass |  |  | 9999 |  |  | 3 |  |  |  | 3.3 | Pass | 3.3 | Pass | 3.1 | Pass | 3.2 | Pass | 2.8 | Pass | 2.9 | Pass | 3.3 | Pass | 3.07 | Pass | 2.7 | Pass | 3.16 | Pass | 3.19 | Pass | 3.37 | Pass | 3.9 | Pass
21 | 7.7 | 7.3 | 7.1 | 3.3 | PASS | 2.7 | Pass |  |  | 13.6 |  |  | 3.1 |  |  |  | 3.8 | Pass | 2.9 | Pass | 3.4 | Pass | 4 | Pass | 3.7 | Pass | 3.3 | Pass | 3.2 | Pass | 2.96 | Pass | 2.97 | Pass | 3.48 | Pass | 3.39 | Pass | 3.49 | Pass | 3.4 | Pass
22 | 6.1 | 7.7 | 6.7 | 9.6 | WARNING | 9.6 | Warning | 2.6 | Replaced with new one | 18.2 |  |  | 8.4 |  |  |  | 3.3 | Pass | 3.1 | Pass | 2.6 | Pass | 2.8 | Pass | 3 | Pass | 3.1 | Pass | 2.4 | Pass | 3.43 | Pass | 3.42 | Pass | 3.14 | Pass | 3.26 | Pass | 3.34 | Pass | 2.8 | Pass
23 | 6.4 | 2.6 | 9.6 | 8.5 | PASS | 7.5 | Pass |  |  | 19.8 |  |  | 3.4 |  |  |  | 2.9 | Pass | 3.1 | Pass | 2.4 | Pass | 3 | Pass | 3 | Pass | 3.4 | Pass | 2.8 | Pass | 3.39 | Pass | 3.42 | Pass | 3.21 | Pass | 3.36 | Pass | 3.44 | Pass | 3.4 | Pass
24 | 2.8 | 5.8 | 3.1 | 6.3 | PASS | 8.2 | Pass |  |  | 2.6 |  |  | 8.9 |  |  |  | 3.5 | Pass | 3.4 | Pass | 2.9 | Pass | 3.1 | Pass | 3.4 | Pass | 3.5 | Pass | 2.8 | Pass | 3.5 | Pass | 4 | Pass | 3.44 | Pass | 3.55 | Pass | 3.68 | Pass | 3.1 | Pass
25 | 5.2 | 6.4 | 2.9 | 7.6 | PASS | 11.5 | Warning | 2.6 | Replaced with new one | 2.5 |  |  | 10.7 | Warning |  |  | 3 | Pass | 3 | Pass | 2.1 | Pass | 2.9 | Pass | 3 | Pass | 3.4 | Pass | 2.4 | Pass | 3.18 | Pass | 3.21 | Pass | 3.5 | Pass | 3.46 | Pass | 3.55 | Pass | 2.9 | Pass
26 | 5.5 | 7.9 | 8.6 | 7 | PASS | 9.3 | Warning |  | Replacement pending |  | Battery Reading did not come |  | 10 | Warning |  |  | 2.9 | Pass | 3.2 | Pass | 3.3 | Pass | 3.6 | Pass | 2.9 | Pass | 3.3 | Pass | 2.5 | Pass | 3.36 | Pass | 3.05 | Pass | 3.18 | Pass | 3.39 | Pass | 3.46 | Pass | 4.1 | Pass
27 | 6.7 | 8.1 | 8.3 | 7.7 | PASS | 7 | Pass |  |  |  | Battery Reading did not come |  | 8.4 |  |  |  | 3 | Pass | 3.2 | Pass | 3.2 | Pass | 2.9 | Pass | 3 | Pass | 3.2 | Pass | 3.1 | Pass | 3.69 | Pass | 3.07 | Pass | 3.22 | Pass | 3.33 | Pass | 3.46 | Pass | 3.4 | Pass
28 | 7 | 10 | 8.9 | 2.5 | PASS | 5.8 | Pass |  |  |  | Battery Reading did not come |  | 3.8 |  |  |  | 3.2 | Pass | 3.1 | Pass | 3.1 | Pass | 2.4 | Pass | 3.1 | Pass | 3.3 | Pass | 2.8 | Pass | 3.44 | Pass | 3 | Pass | 3.42 | Pass | 3.23 | Pass | 3.69 | Pass | 3.1 | Pass
29 | 8.4 | 6.7 | 8.5 | 6.1 | PASS | 3 | Pass |  |  |  | Battery Reading did not come |  | 3.7 |  |  |  | 2.9 | Pass | 3.3 | Pass | 3 | Pass | 3.1 | Pass | 3.4 | Pass | 2.9 | Pass | 2.5 | Pass | 3.31 | Pass | 2.99 | Pass | 3.37 | Pass | 3.49 | Pass | 3.56 | Pass | 3.5 | Pass
30 | 7.7 | 8.2 | 8.8 | 6.6 | PASS | 8.5 | Pass |  |  |  | Battery Reading did not come |  | 13.3 | Fail |  |  | 3 | Pass | 3.5 | Pass | 3 | Pass | 3 | Pass | 3.5 | Pass | 3 | Pass | 3.9 | Pass | 2.86 | Pass | 3.03 | Pass | 3.19 | Pass | 3.28 | Pass | 3.51 | Pass | 3.6 | Pass
31 | 6.2 | 2.8 | 7.2 | 8.7 | PASS | 6.8 | Pass |  |  |  | Battery Reading did not come |  | 11.1 | Warning |  |  | 3.3 | Pass | 3.2 | Pass | 2.9 | Pass | 3.3 | Pass | 3.6 | Pass | 3.1 | Pass | 3.6 | Pass | 3.45 | Pass | 3.33 | Pass | 3.13 | Pass | 3.3 | Pass | 3.18 | Pass | 2.9 | Pass
32 | 3 | 6.1 | 6.8 | 9.3 | WARNING | 3.3 | Pass |  |  |  | Battery Reading did not come |  | 4 |  |  |  | 3 | Pass | 3.8 | Pass | 2.9 | Pass | 2.4 | Pass | 3.3 | Pass | 3.1 | Pass | 2.6 | Pass | 3.58 | Pass | 2.95 | Pass | 3.15 | Pass | 3.33 | Pass | 3.49 | Pass | 2 | Pass
33 | 7.9 | 5.5 | Made one bank of only 32 good batteries |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 3.4 | Pass | 3.6 | Pass | 3 | Pass | 2.2 | Pass | 3.2 | Pass | 3.4 | Pass | 2.9 | Pass | 2.6 | Pass | 3.33 | Pass | 3.32 | Pass | 3.35 | Pass | 3.64 | Pass | 3.7 | Pass
34 | 5.3 | 8 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.7 | New Battery Installation done today | 3.1 | Pass | 3 | Pass | 3.1 | Pass | 3.3 | Pass | 3.2 | Pass | 3.2 | Pass | 3.5 | Pass | 3.33 | Pass | 3.35 | Pass | 3.29 | Pass | 3.39 | Pass | 3.49 | Pass | 2.8 | Pass
35 | 7.9 | 7 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.7 | New Battery Installation done today | 3.6 | Pass | 3.4 | Pass | 3.4 | Pass | 3.2 | Pass | 3.2 | Pass | 3.6 | Pass | 3.4 | Pass | 3.28 | Pass | 3.27 | Pass | 3.61 | Pass | 3.7 | Pass | 3.83 | Pass | 3 | Pass
36 | 6.1 | 11.8 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 3 | Pass | 3.6 | Pass | 3.8 | Pass | 6 | Pass | 3.2 | Pass | 3.3 | Pass | 3.3 | Pass | 6.74 | Pass | 6.47 | Pass | 3.44 | Pass | 3.47 | Pass | 3.64 | Pass | 3.1 | Pass
37 | 6.6 | 9.4 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 3.6 | Pass | 3.2 | Pass | 3.7 | Pass | 2.4 | Pass | 2.9 | Pass | 3 | Pass | 3.5 | Pass | 4.44 | Pass | 3.48 | Pass | 3.6 | Pass | 3.54 | Pass | 3.89 | Pass | 3.4 | Pass
38 | 8.6 | 9.4 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 3.1 | Pass | 3.2 | Pass | 3.3 | Pass | 2.9 | Pass | 3.2 | Pass | 3.4 | Pass | 3.6 | Pass | 2.74 | Pass | 3.17 | Pass | 3.22 | Pass | 3.22 | Pass | 3.45 | Pass | 3.6 | Pass
39 | 8 | 8.2 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 2.1 | Pass | 3.4 | Pass | 3.2 | Pass | 3.1 | Pass | 3.2 | Pass | 3 | Pass | 2.9 | Pass | 3.46 | Pass | 3.41 | Pass | 3.28 | Pass | 3.37 | Pass | 3.39 | Pass | 3.4 | Pass
40 | 8 | 8.8 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.5 | New Battery Installation done today | 2.9 | Pass | 3.3 | Pass | 2.9 | Pass | 2.5 | Pass | 3.4 | Pass | 3 | Pass | 3.5 | Pass | 3.45 | Pass | 3.42 | Pass | 3.27 | Pass | 3.47 | Pass | 3.5 | Pass | 3.6 | Pass
41 | 6.5 | 8.7 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 2.8 | Pass | 3.1 | Pass | 3.1 | Pass | 2.9 | Pass | 3.4 | Pass | 3.1 | Pass | 3.2 | Pass | 3.34 | Pass | 3.47 | Pass | 3.36 | Pass | 3.41 | Pass | 3.56 | Pass | 3.8 | Pass
42 | 7 | 11.7 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 2.3 | Pass | 2.5 | Pass | 3.1 | Pass | 2.3 | Pass | 3.2 | Pass | 3.3 | Pass | 3.4 | Pass | 3.24 | Pass | 3.01 | Pass | 3.31 | Pass | 3.45 | Pass | 3.36 | Pass | 3.8 | Pass
43 | 9.5 | 2.7 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.7 | New Battery Installation done today | 2.8 | Pass | 2.9 | Pass | 2.9 | Pass | 2.8 | Pass | 3.1 | Pass | 3 | Pass | 2.8 | Pass | 3.26 | Pass | 2.97 | Pass | 3.48 | Pass | 3.38 | Pass | 3.33 | Pass | 3.2 | Pass
44 | 3 | 10.4 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 3 | Pass | 3.1 | Pass | 2.9 | Pass | 3.1 | Pass | 3 | Pass | 3.4 | Pass | 3.2 | Pass | 3.32 | Pass | 2.87 | Pass | 3.5 | Pass | 3.31 | Pass | 3.54 | Pass | 3.1 | Pass
45 | 9 | 9.6 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.5 | New Battery Installation done today | 2.9 | Pass | 3.2 | Pass | 3 | Pass | 3.1 | Pass | 3.1 | Pass | 3 | Pass | 3.5 | Pass | 2.93 | Pass | 3.56 | Pass | 3.52 | Pass | 3.18 | Pass | 3.45 | Pass | 3.3 | Pass
46 | 11.1 | 7.5 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 3.7 | Pass | 4 | Pass | 3.2 | Pass | 3.2 | Pass | 65.9 | Fail | 3.9 | Pass | 3.3 | Pass | 2.99 | Pass | 3.34 | Pass | 5.26 | Pass | 4.82 | Pass | 5.22 | Pass | 2.9 | Pass
47 | 7.2 | 12.4 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.7 | New Battery Installation done today | 3.1 | Pass | 4 | Pass | 4.1 | Pass | 3.2 | Pass | 3.1 | Pass | 3.3 | Pass | 5.9 | Pass | 3.28 | Pass | 3.18 | Pass | 3.5 | Pass | 3.28 | Pass | 3.84 | Pass | 4.5 | Pass
48 | 7.5 | 8.2 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 2.6 | Pass | 3.1 | Pass | 3.2 | Pass | 3.3 | Pass | 3.3 | Pass | 3 | Pass | 2.4 | Pass | 3.06 | Pass | 3.12 | Pass | 3.44 | Pass | 3.43 | Pass | 3.05 | Pass | 4.8 | Pass
49 | 6.3 | 2.9 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 2.9 | Pass | 3.2 | Pass | 3.1 | Pass | 2.8 | Pass | 2.9 | Pass | 3.1 | Pass | 3.1 | Pass | 3.31 | Pass | 3.18 | Pass | 3.13 | Pass | 3.29 | Pass | 3.08 | Pass | 2.6 | Pass
50 | 2.8 | 10.2 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.7 | New Battery Installation done today | 2.9 | Pass | 2.8 | Pass | 2.8 | Pass | 3.3 | Pass | 3.2 | Pass | 3.2 | Pass | 2.4 | Pass | 3.37 | Pass | 3.79 | Pass | 3.08 | Pass | 3.45 | Pass | 3.3 | Pass | 2.7 | Pass
51 | 8.8 | 19.9 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.7 | New Battery Installation done today | 3.3 | Pass | 3.1 | Pass | 2.8 | Pass | 8.2 | Pass | 3 | Pass | 3.1 | Pass | 2.8 | Pass | 5.47 | Pass | 4.76 | Pass | 3.56 | Pass | 3.59 | Pass | 3.62 | Pass | 3.3 | Pass
52 | 10.9 | 20 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 3.3 | Pass | 3.5 | Pass | 3.1 | Pass | 2.3 | Pass | 3.2 | Pass | 3.1 | Pass | 3.1 | Pass | 2.98 | Pass | 2.52 | Pass | 3.38 | Pass | 3.38 | Pass | 3.44 | Pass | 3.4 | Pass
53 | 7.8 | 11.3 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 2.6 | Pass | 3.2 | Pass | 3.4 | Pass | 2.8 | Pass | 3 | Pass | 2.8 | Pass | 3.2 | Pass | 2.83 | Pass | 2.55 | Pass | 3.33 | Pass | 3.37 | Pass | 3.46 | Pass | 2.9 | Pass
54 | 6.9 | 7.6 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 3.1 | Pass | 3.3 | Pass | 3.1 | Pass | 3 | Pass | 2.9 | Pass | 2.5 | Pass | 3.4 | Pass | 2.79 | Pass | 3.17 | Pass | 3.28 | Pass | 3.22 | Pass | 3.34 | Pass | 2.6 | Pass
55 | 5.9 | 6.3 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.7 | New Battery Installation done today | 2.8 | Pass | 3 | Pass | 3.3 | Pass | 3.3 | Pass | 3.3 | Pass | 3.1 | Pass | 2.7 | Pass | 3.13 | Pass | 2.86 | Pass | 3.12 | Pass | 3.27 | Pass | 3.4 | Pass | 3.5 | Pass
56 | 7.8 | 10.6 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 3.2 | Pass | 2.8 | Pass | 2.8 | Pass | 3.1 | Pass | 3.6 | Pass | 3.3 | Pass | 3.4 | Pass | 3.3 | Pass | 3.09 | Pass | 3.25 | Pass | 3.43 | Pass | 3.4 | Pass | 3.2 | Pass
57 | 6.6 | 7.6 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 3.2 | Pass | 3.3 | Pass | 3.1 | Pass | 3.6 | Pass | 3.4 | Pass | 3.5 | Pass | 2.4 | Pass | 3.35 | Pass | 3.11 | Pass | 3.58 | Pass | 3.85 | Pass | 3.71 | Pass | 3.9 | Pass
58 | 3 | 2.7 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 3.3 | Pass | 3.7 | Pass | 3.7 | Pass | 3.2 | Pass | 3.1 | Pass | 3.3 | Pass | 2.9 | Pass | 3.44 | Pass | 3.23 | Pass | 3.27 | Pass | 3.28 | Pass | 3.24 | Pass | 3.3 | Pass
59 | 6.8 | 7.6 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 2.6 | Pass | 3 | Pass | 2.9 | Pass | 3.1 | Pass | 2.9 | Pass | 3.4 | Pass | 2.7 | Pass | 3.05 | Pass | 2.73 | Pass | 3.14 | Pass | 3.33 | Pass | 3.28 | Pass | 3.5 | Pass
60 | 3.1 | 2.5 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 3.6 | Pass | 2.9 | Pass | 3.2 | Pass | 3.3 | Pass | 3.2 | Pass | 3.2 | Pass | 3.5 | Pass | 3.72 | Pass | 3.36 | Pass | 3.48 | Pass | 3.15 | Pass | 3.77 | Pass | 4 | Pass
61 | 8.9 | 9.2 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 6.2 | New Battery Installation done today | 5.7 | Pass | 3 | Pass | 3.1 | Pass | 2.5 | Pass | 5.7 | Pass | 6.3 | Pass | 3.2 | Pass | 3.22 | Pass | 3 | Pass | 7 | Pass | 6.98 | Pass | 7.42 | Pass | 8 | Pass
62 | 7.5 | 7.8 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.5 | New Battery Installation done today | 3.1 | Pass | 5.6 | Pass | 6.3 | Pass | 2.9 | Pass | 3.1 | Pass | 3.4 | Pass | 3 | Pass | 3.47 | Pass | 3 | Pass | 3.22 | Pass | 3.35 | Pass | 3.33 | Pass | 2.4 | Pass
63 | 6.5 | 6.8 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.7 | New Battery Installation done today | 3.3 | Pass | 3.5 | Pass | 2.9 | Pass | 2.8 | Pass | 3.2 | Pass | 3.4 | Pass | 3.2 | Pass | 3.37 | Pass | 3.24 | Pass | 3.3 | Pass | 3.55 | Pass | 3.47 | Pass | 2.7 | Pass
64 | 6.2 | 7.4 |  |  |  |  | Disconnected - Gone Bad Last Year | [7 empty] | 2.6 | New Battery Installation done today | 2.6 | Pass | 3 | Pass | 3.3 | Pass | 3.5 | Pass | 3.3 | Pass | 3.4 | Pass | 6.1 | Pass | 3.42 | Pass | 3.74 | Pass | 3.35 | Pass | 3.48 | Pass | 3.59 | Pass | 2.7 | Pass
[35 empty] | 64 | Pass | 64 | Pass | 64 | Pass | 64 | Pass
[35 empty] | 0 | Warning | 0 | Warning | 0 | Warning | 0 | Warning
[35 empty] | 0 | Fail | 0 | Fail | 0 | Fail | 0 | Fail
[35 empty] | 0 | Non-Healthy Batteries | 0 | Non-Healthy Batteries | 0 | Non-Healthy Batteries | 0 | Non-Healthy Batteries

## MICRO 1 & 2
Battery Spec: 12 Volts 120 AH
Brand: Exide Powersafe
Sr. No. | 2017-07-21 | 17/11/2017 | 23/1/2018 | Comments | 2018-03-07 | Comments | 24/10/2018 | Comments - 24/10/2018 | 21/1/2019 | Comments - 21/1/2019 | 19/8/2019 | Comments - 19/8/2019 | 27/9/2019 | Comments - 27/9/2019 | 31/10/2019 | Comments - 31/10/2019 | 26/11/2019 | Comments - 26/11/2019 | 2020-08-01 | Comments - 8/1/2020 | 14/2/2020 | Comments - 14/2/2020 | 2020-07-12 | Comments - 7/12/2020 | 28/1/2021 | Comments - 28/1/2021 | 29/1/2021 | 17/2/2021 | Comments - 17/2/2021 | 2021-09-03 | Comments - 9/3/2021
1 | 5.8 | 6.5 | 6.3 | PASS | 7.1 | Pass | 8.1 | Pass | 8.6 | Pass | 6.3 | Pass | 8 | Pass | 3.6 |  | 70.2 | Fail | 6.86 | Pass | 7.4 | Pass | 5.47 | Pass |  |  | Changed | 4.37 | Pass | 3.9 | Pass
2 | 6.2 | 5.7 | 6 | PASS | 7.4 | Pass | 8.7 | Pass | 9.1 | Warning | 6.3 | Pass | 51.6 | Fail | 4.5 |  | 3.9 | Pass | 5.13 | Pass | 9999 | Fail | 4.56 | Pass |  |  | Changed | 3.91 | Pass | 3.9 | Pass
3 | 5.5 | 5.9 | 5.8 | PASS | 7.3 | Pass | 8.2 | Pass | 8.4 | Pass | 5 | Pass | 8.3 | Pass | 9.9 | Warning | 53.7 | Fail | 16.21 | Fail | 26.9 | Fail | 4.19 | Pass |  |  | Changed | 3.88 | Pass | 3.9 | Pass
4 | 6 | 5.5 | 6 | PASS | 7.2 | Pass | 7.9 | Pass | 8.5 | Pass | 4.4 | Pass | 21.2 | Fail | 11.6 | Warning | 3.9 | Pass |  | No Reading Came | 9999 | Fail | 5.3 | Pass |  |  | Changed | 4.04 | Pass | 3.66 | Pass
5 | 5.6 | 5.1 | 6.3 | PASS | 7.2 | Pass | 7.9 | Pass | 8.2 | Pass | 4.1 | Pass | 5.4 |  | 4 |  | 6 | Pass | 7.46 | Pass | 5.14 | Pass | 4.16 | Pass |  |  | Changed | 4.23 | Pass | 4.21 | Pass
6 | 6.4 | 5.7 | 6.3 | PASS | 7.9 | Pass | 8.9 | Pass | 9.6 | Warning | 4.5 | Pass | 7.8 |  | 4.4 |  | 4 | Pass | 4.1 | Pass | 5.21 | Pass | 11.63 | Warning |  |  | Changed | 4.06 | Pass | 4.32 | Pass
7 | 5.4 | 5.1 | 5.4 | PASS | 6.8 | Pass | 7.7 | Pass | 7.5 | Pass | 3.9 | Pass | 5 |  | 5.8 |  | 3.7 | Pass | 3.92 | Pass | 4.81 | Pass | 5.11 | Pass |  |  | Changed | 5.64 | Pass | 5.04 | Pass
8 | 6 | 5.8 | 6.4 | PASS | 8.5 | Pass | 9.5 | Warning | 10.6 | Warning | 5.1 | Pass | 4.2 |  | 6.7 |  | 4.1 | Pass | 6.09 | Pass | 5.97 | Pass | 4.09 | Pass |  |  | Changed | 4.75 | Pass | 4.8 | Pass
9 | 6.1 | 6.2 | 6.9 | PASS | 8.6 | Pass | 9.8 | Warning | 10.5 | Warning | 4.3 | Pass | 4.1 |  | 3.9 |  | 3.6 | Pass | 3.93 | Pass | 9999 | Fail | 4.62 | Pass |  |  | Changed | 4.91 | Pass | 4.28 | Pass
10 | 6.3 | 5.6 | 5.9 | PASS | 7.8 | Pass | 8.9 | Pass | 9.2 | Warning | 4.9 | Pass | 4.5 |  | 3.9 |  | 4 | Pass |  | No Reading Came | 4.05 | Pass | 4.05 | Pass |  |  | Changed | 4.18 | Pass | 3.87 | Pass
11 | 5.6 | 6 | 6.6 | PASS | 8.2 | Pass | 9.8 | Pass | 10.4 | Warning | 11.4 | Warning | 49.7 | Fail | 4.2 |  | 69 | Fail |  | No Reading Came | 4.16 | Pass | 4.17 | Pass |  |  | Changed | 4.37 | Pass | 3.88 | Pass
12 | 5.8 | 5.4 | 5.9 | PASS | 7.4 | Pass | 7.9 | Pass | 8.5 | Pass | 5.4 | Pass | 5.8 |  | 4.3 |  | 6.8 | Pass | 4.21 | Pass | 9999 | Fail | 9999 | Fail |  |  | Changed | 3.97 | Pass | 3.88 | Pass
13 | 5.5 | 5.4 | 5.7 | PASS | 7 | Pass | 7.9 | Pass | 8 | Pass | 4.4 | Pass | 7 |  | 7.2 |  | 7.7 | Pass | 4.04 | Pass | 4.09 | Pass | 4.79 | Pass |  |  | Changed | 4.61 | Pass | 4.29 | Pass
14 | 5.6 | 5 | 5.7 | PASS | 6.7 | Pass | 8.8 | Pass | 7.4 | Pass | 4.9 | Pass | 4.1 |  | 4.9 |  | 3.9 | Pass | 4.16 | Pass | 3.99 | Pass | 28.97 | Fail |  |  | Changed | 3.93 | Pass | 3.76 | Pass
15 | 5.7 | 5.6 | 6 | PASS | 7.8 | Pass | 7.9 | Pass | 9.1 | Warning | 5 | Pass | 5.7 |  | 5.8 |  | 5.6 | Pass | 3.97 | Pass | 9999 | Fail | 9.24 | Warning |  |  | Changed | 4.03 | Pass | 3.85 | Pass
16 | 6.1 | 5.2 | 5.6 | PASS | 6.8 | Pass | 7.6 | Pass | 8.9 | Pass | 3.9 | Pass | 5.8 |  | 4.9 |  | 3.9 | Pass | 4.04 | Pass | 5.15 | Pass | 5.25 | Pass |  |  | Changed | 3.82 | Pass | 3.82 | Pass
17 | 5.9 | 5.3 | 5.6 | PASS | 6.5 | Pass | 7.5 | Pass | 8.2 | Pass | 4.8 | Pass | 4 |  | 6.3 |  | 4 | Pass | 4.04 | Pass | 9999 | Fail | 5.55 | Pass |  |  | Changed | 3.93 | Pass | 3.93 | Pass
18 | 5.9 | 5.3 | 5.7 | PASS | 6.8 | Pass | 9.2 | Warning | 7.9 | Pass | 4.5 | Pass | 3.9 |  | 10.6 | Warning | 4.1 | Pass | 4 | Pass | 9999 | Fail | 7.3 | Pass |  |  | Changed | 3.78 | Pass | 3.81 | Pass
19 | 5.7 | 5.9 | 6.4 | PASS | 7.7 | Pass | 9.5 | Warning | 10.3 | Warning | 5 | Pass | 4 |  | 6.1 |  | 5.9 | Pass | 4.09 | Pass | 17.16 | Fail | 4.22 | Pass |  |  | Changed | 4.17 | Pass | 4.1 | Pass
20 | 5.4 | 5.7 | 6.7 | PASS | 7.9 | Pass | 9.9 | Warning | 10.3 | Warning | 4 | Pass | 3.9 |  | 6.2 |  | 4.1 | Pass | 3.98 | Pass | 16.81 | Fail | 4.12 | Pass |  |  | Changed | 3.89 | Pass | 3.75 | Pass
21 | 5.7 | 5.9 | 6.5 | PASS | 7.9 | Pass | 9.3 | Warning | 10 | Warning | 4.1 | Pass | 4.1 |  | 4.8 |  | 4.5 | Pass | 4.18 | Pass | 9999 | Fail | 4.16 | Pass |  |  | Changed | 3.83 | Pass | 3.86 | Pass
22 | 5.7 | 6.2 | 6.7 | PASS | 8.1 | Pass | 9.9 | Warning | 10.9 | Warning | 4.2 | Pass | 4.1 |  | 14.9 | Fail | 32 | Fail | 4.21 | Pass | 5.26 | Pass | 4.07 | Pass |  |  | Changed | 3.83 | Pass | 3.83 | Pass
23 | 5.7 | 5.6 | 6 | PASS | 7.1 | Pass | 8.4 | Pass | 9.3 | Warning | 4.4 | Pass | 4.1 |  | 4 |  | 4.6 | Pass | 4.08 | Pass | 21.94 | Fail | 9999 | Fail |  |  | Changed | 3.73 | Pass | 3.72 | Pass
24 | 5.6 | 5.4 | 6.4 | PASS | 7.2 | Pass | 8.4 | Pass | 9.1 | Warning | 5.6 | Pass | 4.3 |  | 4.3 |  | 5.2 | Pass | 4.38 | Pass | 6.85 | Pass | 6.3 | Pass |  |  | Changed | 7.3 | Pass | 7.06 | Pass
25 | 5.7 | 6.2 | 6.6 | PASS | 8.3 | Pass | 8.9 | Pass | 9.8 | Warning | 5.1 | Pass | 4.2 |  | 4.3 |  | 5.8 | Pass | 4.22 | Pass | 24.44 | Fail | 4.52 | Pass |  |  | Changed | 3.65 | Pass | 3.63 | Pass
26 | 5.7 | 5.6 | 6 | PASS | 7.8 | Pass | 8.4 | Pass | 9.1 | Warning | 4.1 | Pass | 4 |  | 5.4 |  | 4 | Pass | 4.08 | Pass | 5.66 | Pass | 4.56 | Pass |  |  | Changed | 3.79 | Pass | 3.85 | Pass
27 | 5.8 | 5.7 | 6.2 | PASS | 7.6 | Pass | 8.5 | Pass | 9 | Warning | 4.5 | Pass | 4.4 |  | 5.8 |  | 4 | Pass | 4.02 | Pass | 6.08 | Pass | 4 | Pass |  |  | Changed | 3.84 | Pass | 3.84 | Pass
28 | 5.9 | 6 | 6.5 | PASS | 8.7 | Pass | 9.5 | Warning | 10.6 | Warning | 3.9 | Pass | 4 |  | 6.6 |  | 4 | Pass | 5.84 | Pass | 5.45 | Pass | 4.13 | Pass |  |  | Changed | 3.74 | Pass | 3.8 | Pass
29 | 5.6 | 6 | 6.5 | PASS | 8.4 | Pass | 9.2 | Warning | 10.2 | Warning | 4.1 | Pass | 4.1 |  | 5.3 |  | 4.1 | Pass | 4.13 | Pass | 6.12 | Pass | 4.13 | Pass |  |  | Changed | 3.74 | Pass | 3.65 | Pass
30 | 6 | 6.7 | 6.4 | PASS | 8.5 | Pass | 10 | Warning | 11 | Warning | 5 | Pass | 4.6 |  | 5.1 |  | 4.2 | Pass | 4.18 | Pass | 6.91 | Pass | 4.04 | Pass |  |  | Changed | 4.01 | Pass | 3.8 | Pass
31 | 5.3 | 6 | 6.9 | PASS | 8.2 | Pass | 9.9 | Warning | 10.7 | Warning | 10.6 | Warning | 3.9 |  | 4.7 |  | 11 | Warning | 3.93 | Pass | 5.29 | Pass | 4.09 | Pass |  |  | Changed | 3.76 | Pass | 3.75 | Pass
32 | 5.7 | 5.5 | 5.9 | PASS | 7 | Pass | 8.4 | Pass | 8.6 | Pass | 5.4 | Pass | 3.9 |  | 8.6 |  | 3.9 | Pass | 4.02 | Pass | 9999 | Fail | 4.41 | Pass |  |  | Changed | 4.34 | Pass | 3.75 | Pass
33 | 5.4 | 7 | 7.9 | PASS | 9.8 | Warning | 12 | Failed | 12.8 | Failed | 5 | Pass | 4 |  | 4.1 |  | 4.4 | Pass | 4.1 | Pass | 9999 | Fail | 4.29 | Pass |  |  | Changed | 4 | Pass | 3.65 | Pass
34 | 5.8 | 5.4 | 5.9 | PASS | 6.9 | Pass | 8.4 | Pass | 8.4 | Pass | 5 | Pass | 4.1 |  | 4.9 |  | 18.8 | Fail | 4.18 | Pass | 5.2 | Pass | 7.67 | Pass |  |  | Changed | 4.11 | Pass | 3.99 | Pass
35 | 5.6 | 5.6 | 6 | PASS | 7.2 | Pass | 8.2 | Pass | 8.3 | Pass | 4.5 | Pass | 4 |  | 4.2 |  | 5 | Pass | 4.22 | Pass | 9999 | Fail | 4.89 | Pass |  |  | Changed | 4.02 | Pass | 3.84 | Pass
36 | 6 | 5.7 | 6.4 | PASS | 7.3 | Pass | 8.8 | Pass | 9.2 | Warning | 5.2 | Pass | 4.1 |  | 4.1 |  | 23.9 | Fail | 4.11 | Pass | 5.06 | Pass | 23.46 | Fail |  |  | Changed | 7.47 | Pass | 7.28 | Pass
37 | 5.7 | 5.3 | 5.8 | PASS | 7 | Pass | 7.6 | Pass | 7.9 | Pass | 5.1 | Pass | 4.2 |  | 4 |  | 4 | Pass | 4.23 | Pass | 5.32 | Pass | 4.2 | Pass |  |  | Changed | 3.79 | Pass | 3.66 | Pass
38 | 5.6 | 5.8 | 6.4 | PASS | 7.8 | Pass | 9.7 | Warning | 10.1 | Warning | 5.5 | Pass | 3.9 |  | 4 |  | 3.9 | Pass | 4.03 | Pass | 6.33 | Pass | 26.5 | Fail |  |  | Changed | 3.88 | Pass | 3.84 | Pass
39 | 5.3 | 7.1 | 7.1 | PASS | 9.2 | Warning | 10.3 | Warning | 11.1 | Warning | 4 | Pass | 4 |  | 3.9 |  | 4.2 | Pass | 4.06 | Pass | 26.11 | Fail | 4.27 | Pass |  |  | Changed | 4.09 | Pass | 4 | Pass
40 | 5.9 | 5.6 | 6.2 | PASS | 7 | Pass | 8.5 | Pass | 8.5 | Pass | 4 | Pass | 3.9 |  | 4.3 |  | 4.1 | Pass | 4.11 | Pass | 9999 | Fail | 4.27 | Pass |  |  | Changed | 3.79 | Pass | 3.79 | Pass
41 | 5.4 | 5.8 | 6.5 | PASS | 8.4 | Pass | 9.8 | Warning | 10.8 | Warning | 8.7 | Pass | 4 |  | 5.7 |  | 5.2 | Pass | 4.1 | Pass | 9999 | Fail | 4.13 | Pass |  |  | Changed | 3.9 | Pass | 3.84 | Pass
42 | 5.4 | 5.2 | 5.9 | PASS | 7.3 | Pass | 8.8 | Pass | 9.6 | Warning | 5.2 | Pass | 4.1 |  | 5.8 |  | 6.6 | Pass | 5.11 | Pass | 5.81 | Pass | 4.03 | Pass |  |  | Changed | 3.94 | Pass | 3.88 | Pass
43 | 5.6 | 6.1 | 6.7 | PASS | 9.1 | Warning | 10.7 | Warning | 12.3 | Warning | 5.1 | Pass | 5.2 |  | 6 |  | 5.1 | Pass | 4.12 | Pass | 5.18 | Pass | 4.19 | Pass |  |  | Changed | 3.82 | Pass | 3.74 | Pass
44 | 5.6 | 5.7 | 5.9 | PASS | 7.2 | Pass | 8.3 | Pass | 8.7 | Pass | 6 | Pass | 7.2 |  | 5.4 |  | 5.7 | Pass | 3.99 | Pass | 6.91 | Pass | 7.89 | Pass |  |  | Changed | 4.08 | Pass | 4.04 | Pass
45 | 5.7 | 6.2 | 6.5 | PASS | 8.5 | Pass | 9.5 | Warning | 10.6 | Warning | 5 | Pass | 4 |  | 3.7 |  | 66.7 | Fail | 4.12 | Pass | 5.68 | Pass | 4.46 | Pass |  |  | Changed | 4.55 | Pass | 4.06 | Pass
46 | 5.6 | 5.6 | 6.3 | PASS | 7.4 | Pass | 9.2 | Warning | 9.6 | Warning | 4.1 | Pass | 3.6 |  | 4 |  | 5.8 | Pass | 4.01 | Pass | 6.92 | Pass | 6.25 | Pass |  |  | Changed | 4.77 | Pass | 4.01 | Pass
47 | 5.8 | 5.5 | 6.1 | PASS | 7 | Pass | 8.5 | Pass | 9.2 | Warning | 5 | Pass | 5.8 |  | 4.1 |  | 5.9 | Pass | 4.09 | Pass | 5.8 | Pass | 9999 | Fail |  |  | Changed | 4.17 | Pass | 4.84 | Pass
48 | 5.6 | 5.2 | 6 | PASS | 6.9 | Pass | 8.5 | Pass | 9.4 | Warning | 4.5 | Pass | 3.9 |  | 4 |  | 28.4 | Fail | 4.1 | Pass | 9999 | Fail | 4.23 | Pass |  |  | Changed | 4.8 | Pass | 4.21 | Pass
49 | 5.5 | 5.9 | 6.4 | PASS | 7.5 | Pass | 9.3 | Warning | 10.1 | Warning | 4.7 | Pass | 3.9 |  | 3.9 |  | 5.8 | Pass | 6.93 | Pass | 6.4 | Pass | 4.08 | Pass |  |  | Changed | 4.4 | Pass | 4 | Pass
50 | 6.2 | 5.3 | 5.9 | PASS | 7.1 | Pass | 8.7 | Pass | 9.4 | Warning | 6.8 | Pass | 5.2 |  | 4.3 |  | 16.3 | Fail | 5.76 | Pass | 9999 | Fail | 4.26 | Pass |  |  | Changed | 4.85 | Pass | 3.75 | Pass
51 | 5.5 | 6.3 | 7.1 | PASS | 9.2 | Warning | 11 | Warning | 12.4 | Failed | 5.7 | Pass | 6.5 |  | 4 |  | 4.1 | Pass | 4.1 | Pass | 12.24 | Fail | 4.25 | Pass |  |  | Changed | 4.07 | Pass | 3.6 | Pass
52 | 5.8 | 5.7 | 6.3 | PASS | 8 | Pass | 9.6 | Warning | 10.1 | Warning | 5.7 | Pass | 7.3 |  | 4.4 |  | 4 | Pass |  | No Reading Came | 9999 | Fail | 4.16 | Pass |  |  | Changed | 4.99 | Pass | 3.93 | Pass
53 | 5.5 | 6 | 6.6 | PASS | 8.4 | Pass | 10.1 | Warning | 10.7 | Warning | 4 | Pass | 4 |  | 4.3 |  | 4 | Pass | 4.08 | Pass | 5.58 | Pass | 6.27 | Pass |  |  | Changed | 5.44 | Pass | 3.99 | Pass
54 | 5.6 | 5.4 | 5.9 | PASS | 7 | Pass | 8.3 | Pass | 9.2 | Warning | 4 | Pass | 4 |  | 4.5 |  | 4.1 | Pass | 4.14 | Pass | 8.27 | Pass | 5.27 | Pass |  |  | Changed | 5.11 | Pass | 3.96 | Pass
55 | 5.9 | 6 | 6.7 | PASS | 8.7 | Pass | OFF | Failed | 9999 | Failed | 5.3 | Pass | 4 |  | 4.2 |  | 4.2 | Pass | 4.11 | Pass | 21.22 | Fail | 5.43 | Pass |  |  | Changed | 4.62 | Pass | 3.98 | Pass
56 | 5.3 | 6.1 | 6.7 | PASS | 8.3 | Pass | 9.2 | Warning | 10.5 | Warning | 6.3 | Pass | 7.2 |  | 4 |  | 19.1 | Fail | 4.18 | Pass | 9999 | Fail | 4.04 | Pass |  |  | Changed | 4.32 | Pass | 4.01 | Pass
57 | 5.4 | 6.3 | 7 | PASS | 8.4 | Pass | 10 | Warning | 11.4 | Warning | 7.3 | Pass | 3.9 |  | 4.2 |  | 7.3 | Pass | 4.38 | Pass | 9999 | Fail | 9999 | Fail |  |  | Changed | 4.23 | Pass | 3.75 | Pass
58 | 5.9 | 6.1 | 6.7 | PASS | 8.5 | Pass | 9.7 | Warning | 11.5 | Warning | 4.9 | Pass | 3.9 |  | 4.2 |  | 11.9 | Warning | 4.07 | Pass | 5.79 | Pass | 5.29 | Pass |  |  |  | 3.88 | Pass | 3.63 | Pass
59 | 5.3 | 5.9 | 6.6 | PASS | 8.4 | Pass | 10.7 | Warning | 10.4 | Warning | 4.9 | Pass | 5.3 |  | 4 |  | 83 | Fail | 4 | Pass | 6.65 | Pass | 4.14 | Pass |  |  |  | 3.79 | Pass | 3.7 | Pass
60 | 5.6 | 5.7 | 6.4 | PASS | 8.5 | Pass | 10.8 | Warning | 9.6 | Warning | 6.2 | Pass | 7.2 |  | 3.7 |  | 20.4 | Fail | 4.03 | Pass | 9999 | Fail | 4.19 | Pass |  |  |  | 5.26 | Pass | 3.77 | Pass
61 | 5.6 | 5.4 | 6.1 | PASS | 7.5 | Pass | 10 | Warning | 8.6 | Pass | 4.7 | Pass | 4 |  | 4.7 |  | 4.1 | Pass | 4.03 | Pass | 5.19 | Pass | 28.12 | Fail |  |  |  | 5.79 | Pass | 4.09 | Pass
62 | 5.2 | 5.9 | 6.4 | PASS | 8.1 | Pass | 8.3 | Pass | 9.5 | Warning | 5.1 | Pass | 4 |  | 4.4 |  | 3.9 | Pass | 4.42 | Pass | 5.61 | Pass | 4.3 | Pass |  |  |  | 4.41 | Pass | 4.52 | Pass
63 | 5.7 | 5.4 | 6.1 | PASS | 7.4 | Pass | 8.5 | Pass | 8.7 | Pass | 4.3 | Pass | 3.9 |  | 4 |  | 3.9 | Pass | 5.65 | Pass | 5.74 | Pass | 4.02 | Pass |  |  |  | 4.27 | Pass | 4.22 | Pass
64 | 5.1 | 5.8 | 6.4 | PASS | 8.2 | Pass | 8.4 | Pass | 9.6 | Warning | 4.8 | Pass | 3.9 |  | 4.1 |  | 3.9 | Pass | 5.33 | Pass | 5.17 | Pass | 17.72 | Fail |  |  |  | 4.18 | Pass | 4.17 | Pass
65 | 5 | 5.4 | 5.9 | PASS | 7.3 | Pass | 9.1 | Warning | 8.7 | Pass | 4 | Pass | 3.9 |  | 4.3 |  | 3.8 | Pass |  | No Reading Came | 9999 | Fail | 5.08 | Pass |  |  |  | 4.21 | Pass | 4.17 | Pass
66 | 5.5 | 7 | 7.5 | PASS | 9.7 | Warning | 8.3 | Pass | 12.8 | Failed | 8.3 | Pass | 3.9 |  | 7.4 |  | 3.8 | Pass | 3.96 | Pass | 9999 | Fail | 7.18 | Pass |  |  |  | 4.91 | Pass | 4.08 | Pass
67 | 6.1 | 5.2 | 5.9 | PASS | 7.5 | Pass | 11.3 | Warning | 8.4 | Pass | 6.8 | Pass | 7.8 |  | 4.3 |  | 4.5 | Pass | 4.09 | Pass | 7.4 | Pass | 5.21 | Pass |  |  |  | 4.43 | Pass | 4.16 | Pass
68 | 5.6 | 6.3 | 7.1 | PASS | 9.6 | Warning | 8.2 | Pass | 11.1 | Warning | 4.2 | Pass | 4 |  | 4.1 |  | 5.3 | Pass | 4.17 | Pass | 5.46 | Pass | 4.38 | Pass |  |  |  | 4.38 | Pass | 4.16 | Pass
69 | 5.1 | 6.6 | 6.8 | PASS | 8.8 | Pass | 9.9 | Warning | 10.4 | Warning | 4.3 | Pass | 3.9 |  | 3.9 |  | 3.8 | Pass | 4.05 | Pass | 4.12 | Pass | 24.54 | Fail |  |  |  | 4.46 | Pass | 4.38 | Pass
70 | 5.5 | 6.8 | 7 | PASS | 9.3 | Warning | 9.7 | Warning | 10.4 | Warning | 5 | Pass | 3.9 |  | 3.4 |  | 3.7 | Pass | 4.08 | Pass | 5.99 | Pass | 9999 | Fail |  |  |  | 4.02 | Pass | 4.07 | Pass
71 | 5.5 | 5.6 | 6.1 | PASS | 7.7 | Pass | 9.7 | Warning | 9.2 | Warning | 6.1 | Pass | 3.9 |  | 3.9 |  | 3.8 | Pass | 4.07 | Pass | 9999 | Fail | 9999 | Fail |  |  |  | 4.13 | Pass | 4.12 | Pass
72 | 4.9 | 5.6 | 6.4 | PASS | 9.1 | Warning | 7.6 | Pass | 11 | Warning | 20 | Fail | 4 |  | 7.7 |  | 17.5 | Fail | 4.1 | Pass | 9999 | Fail | 4.24 | Pass |  |  |  | 6.99 | Pass | 7.07 | Pass
73 | 5.1 | 5.8 | 6 | PASS | 7.8 | Pass | 9.7 | Warning | 9.3 | Warning | 3.9 | Pass | 4 |  | 4.9 |  | 4.3 | Pass | 4.01 | Pass | 5.03 | Pass | 9.95 | Warning |  |  |  | 4.27 | Pass | 4.2 | Pass
74 | 5.9 | 5.3 | 5.8 | PASS | 7.4 | Pass | 9.4 | Warning | 9 | Warning | 10.2 | Warning | 3.9 |  | 9.9 | Warning | 3.9 | Pass | 4.03 | Pass | 9999 | Fail | 5.54 | Pass |  |  |  | 4.79 | Pass | 4.02 | Pass
75 | 5.5 | 5.4 | 5.7 | PASS | 7.5 | Pass | 10.3 | Warning | 8.1 | Pass | 7.5 | Pass | 4.3 |  | 8.5 |  | 4.1 | Pass | 4.05 | Pass | 4.62 | Pass | 9999 | Fail |  |  |  | 4.11 | Pass | 4.1 | Pass
76 | 5.2 | 6 | 6.5 | PASS | 7.8 | Pass | 9.8 | Warning | 10.3 | Warning | 4.6 | Pass | 4.1 |  | 4.8 |  | 4.1 | Pass | 4.05 | Pass | 4.81 | Pass | 4.49 | Pass |  |  |  | 4.17 | Pass | 4.03 | Pass
77 | 5.4 | 6 | 6.8 | PASS | 9.2 | Warning | 9.5 | Warning | 11.5 | Warning | 5 | Pass | 5.1 |  | 4.5 |  | 3.9 | Pass | 3.96 | Pass | 5.24 | Pass | 4.07 | Pass |  |  |  | 4.07 | Pass | 4.15 | Pass
78 | 5.3 | 5.7 | 6.5 | PASS | 8.2 | Pass | 7.6 | Pass | 9.9 | Warning | 5.9 | Pass | 6.2 |  | 5.8 |  | 3.9 | Pass | 4.03 | Pass | 5.49 | Pass | 4.11 | Pass |  |  |  | 4.11 | Pass | 4.1 | Pass
79 | 5.3 | 5.8 | 6.5 | PASS | 8.8 | Pass | 8.2 | Pass | 10.3 | Warning | 4.2 | Pass | 28.4 | Fail | 7.5 |  | 4 | Pass | 4.05 | Pass | 9999 | Fail | 9999 | Fail |  |  |  | 4.09 | Pass | 4.13 | Pass
80 | 5 | 5.2 | 5.6 | PASS | 7.6 | Pass | 8.6 | Pass | 8.3 | Pass | 5.3 | Pass | 5.4 |  | 4 |  | 3.9 | Pass | 3.95 | Pass | 6.16 | Pass | 4.18 | Pass |  |  |  | 4.17 | Pass | 4.03 | Pass
81 | 6.1 | 5.6 | 6.3 | PASS | 8.6 | Pass | 10 | Warning | 10.4 | Warning | 4 | Pass | 6.5 |  | 4 |  | 3.9 | Pass | 3.95 | Pass | 9999 | Fail | 4.18 | Pass |  |  |  | 4.06 | Pass | 4.17 | Pass
82 | 5.5 | 5.5 | 6 | PASS | 8.3 | Pass | 8.5 | Pass | 9.9 | Warning | 3.9 | Pass | 5.2 |  | 4.1 |  | 4.1 | Pass | 3.98 | Pass | 5.87 | Pass | 4.17 | Pass |  |  |  | 9999 | Fail | 4.03 | Pass
83 | 5.2 | 5.7 | 6.3 | PASS | 8.6 | Pass | 9.2 | Warning | 10.7 | Warning | 4.4 | Pass | 4.5 |  | 4.7 |  | 4.2 | Pass | 4.2 | Pass | 9999 | Fail | 4.06 | Pass |  |  |  | 4.28 | Pass | 9999 | Fail
84 | 5.8 | 5.1 | 5.5 | PASS | 7.8 | Pass | 8.5 | Pass | 8.2 | Pass | 4.9 | Pass | 6.7 |  | 6 |  | 5 | Pass | 4.9 | Pass | 6.49 | Pass | 4.29 | Pass |  |  |  | 4.14 | Pass | 4.34 | Pass
85 | 5.3 | 5.5 | 6 | PASS | 7.9 | Pass | 9.5 | Warning | 9.3 | Warning | 4.1 | Pass | 5.1 |  | 5.3 |  | 4 | Pass | 4.04 | Pass | 5.65 | Pass | 6.84 | Pass |  |  |  | 5.8 | Pass | 4.2 | Pass
86 | 5.6 | 5.6 | 6.1 | PASS | 8.2 | Pass | 7.2 | Pass | 9.7 | Warning | 4.2 | Pass | 4.3 |  | 4.9 |  | 4.2 | Pass | 4.48 | Pass | 5.31 | Pass | 5.86 | Pass |  |  |  | 4.09 | Pass | 4.28 | Pass
87 | 5.6 | 5.8 | 6.5 | PASS | 9.1 | Warning | 8.1 | Pass | 10.8 | Warning | 4.5 | Pass | 4.1 |  | 4.9 |  | 4.4 | Pass | 4.38 | Pass | 4.54 | Pass | 7.7 | Pass |  |  |  | 4.12 | Pass | 4.11 | Pass
88 | 5.5 | 5.7 | 6.3 | PASS | 9.1 | Warning | 9 | Warning | 10 | Warning | 4.7 | Pass | 4.1 |  | 5.2 |  | 4 | Pass | 5.11 | Pass | 5.21 | Pass | 8.73 | Pass |  |  |  | 4.13 | Pass | 4.06 | Pass
89 | 5.4 | 5.4 | 5.9 | PASS | 7.7 | Pass | 9.6 | Warning | 9.1 | Warning | 4.8 | Pass | 4 |  | 4.9 |  | 4 | Pass | 5.04 | Pass | 9999 | Fail | 4.55 | Pass |  |  |  | 4.08 | Pass | 17.36 | Fail
90 | 5.4 | 6 | 6.5 | PASS | 9.5 | Warning | 9.1 | Warning | 10.5 | Warning | 4.6 | Pass | 4 |  | 4.2 |  | 3.9 | Pass | 4.01 | Pass | 4.79 | Pass | 9999 | Fail |  |  |  | 4.13 | Pass | 3.99 | Pass
91 | 5.5 | 5.1 | 5.5 | PASS | 7.2 | Pass | 8.1 | Pass | 8.4 | Pass | 4.9 | Pass | 3.9 |  | 4.1 |  | 3.8 | Pass | 3.97 | Pass | 5.88 | Pass | 16.35 | Fail |  |  |  | 4.37 | Pass | 4.29 | Pass
92 | 5.2 | 5.4 | 5.9 | PASS | 8.1 | Pass | 9.4 | Warning | 8.4 | Pass | 5.2 | Pass | 4.1 |  | 4.4 |  | 4.1 | Pass | 4.23 | Pass | 9999 | Fail | 5.13 | Pass |  |  |  | 4.02 | Pass | 3.95 | Pass
93 | 6.3 | 5.1 | 6 | PASS | 8.1 | Pass | 9.1 | Warning | 8.1 | Pass | 32.6 | Fail | 3.9 |  | 3.6 |  | 3.9 | Pass | 4.7 | Pass | 6.22 | Pass | 27.07 | Fail |  |  |  | 4.46 | Pass | 4.28 | Pass
94 | 5.2 | 6 | 5.5 | PASS | 8.6 | Pass | 7.4 | Pass | 9.7 | Warning | 3.6 | Pass | 4.2 |  | 4.3 |  | 4.2 | Pass | 4.31 | Pass | 7.46 | Pass | 4.26 | Pass |  |  |  | 3.96 | Pass | 5.38 | Pass
95 | 5.6 | 6.2 | 6.2 | PASS | 7.5 | Pass | 8.3 | Pass | 9.5 | Warning | 5.6 | Pass | 4.1 |  | 5.5 |  | 3.9 | Pass | 3.91 | Pass | 5.91 | Pass | 4.16 | Pass |  |  |  | 4.21 | Pass | 7.6 | Pass
96 | 5.2 | 6.5 | 6.2 | PASS | 9 | Warning | 9.2 | Warning | 11.1 | Warning | 5.2 | Pass | 6.8 |  | 12.5 | Fail | 3.9 | Pass | 4.14 | Pass | 9999 | Fail | 4.3 | Pass |  |  |  | 5.23 | Pass | 4.19 | Pass
97 | 5.9 | 6.4 | 6.8 | PASS | 9.4 | Warning | 10.5 | Warning | 9.9 | Warning | 6.6 | Pass | 4.1 |  | 19.3 | Fail | 4 | Pass | 4.23 | Pass | 30.46 | Fail | 4.09 | Pass |  |  |  | 5.44 | Pass | 28.17 | Fail
98 | 5.5 | 5.6 | 6.4 | PASS | 8.3 | Pass | 9.1 | Warning | 9.1 | Warning | 8.7 | Pass | 4 |  | 6.4 |  | 4 | Pass | 4.18 | Pass | 25.17 | Fail | 4.13 | Pass |  |  |  | 4.16 | Pass | 4.23 | Pass
99 | 5.4 | 5.7 | 5.9 | PASS | 7.9 | Pass | 8.6 | Pass | 8.1 | Pass | 5.7 | Pass | 4.1 |  | 4 |  | 3.9 | Pass | 4.07 | Pass | 5.2 | Pass | 4.19 | Pass |  |  |  | 4.2 | Pass | 4.25 | Pass
100 | 5.2 | 5.8 | 5.7 | PASS | 8.6 | Pass | 7 | Pass | 9.3 | Warning | 5.5 | Pass | 4.1 |  | 4.1 |  | 3.9 | Pass | 4.13 | Pass | 6 | Pass | 4.16 | Pass |  |  |  | 5.61 | Pass | 4.02 | Pass
101 | 5.5 | 5.5 | 6.3 | PASS | 7.4 | Pass | 7.8 | Pass | 7.8 | Pass | 4.8 | Pass | 3.8 |  | 5.4 |  | 3.8 | Pass | 4.04 | Pass | 6.38 | Pass | 4.15 | Pass |  |  |  | 4.04 | Pass | 4 | Pass
102 | 5 | 5.7 | 5.5 | PASS | 8 | Pass | 7.8 | Pass | 8.7 | Pass | 4.7 | Pass | 62.5 | Fail | 8.4 |  | 3.8 | Pass | 9999 | Fail | 9999 | Fail | 4.24 | Pass |  |  |  | 4.3 | Pass | 4.17 | Pass
103 | 5.4 | 5.7 | 5.8 | PASS | 8.1 | Pass | 7.4 | Pass | 9 | Warning | 8.4 | Pass | 93.9 | Fail | 14.4 | Fail | 3.9 | Pass | 3.96 | Pass | 9999 | Fail | 4.12 | Pass |  |  |  | 6.02 | Pass | 5.61 | Pass
104 | 4.9 | 6 | 6 | PASS | 8.5 | Pass | 8.2 | Pass | 9.5 | Warning | 5.9 | Pass | 37.8 | Fail | 3.8 |  | 5 | Pass | 4.01 | Pass | 16.22 | Fail | 4.19 | Pass |  |  |  | 4.85 | Pass | 4.31 | Pass
105 | 5.9 | 6.3 | 6.3 | PASS | 8.4 | Pass | 8.6 | Pass | 10.8 | Warning | 3.9 | Pass | 4.7 |  | 4.1 |  | 3.7 | Pass |  | No Reading Came | 4.54 | Pass | 9999 | Fail |  |  |  | 5.59 | Pass | 4.25 | Pass
106 | 5 | 5.8 | 6.5 | PASS | 7.2 | Pass | 9.4 | Warning | 8.5 | Pass | 4.6 | Pass | 4.4 |  | 4.1 |  | 3.9 | Pass | 16.91 | Fail | 5.5 | Pass | 6.3 | Pass |  |  |  | 5.36 | Pass | 4.03 | Pass
107 | 5.6 | 5.8 | 5.9 | PASS | 7.7 | Pass | 9.8 | Warning | 9.2 | Warning | 5.4 | Pass | 4.5 |  | 4.3 |  | 7.2 | Pass | 3.95 | Pass | 9999 | Fail | 4.78 | Pass |  |  |  | 5.31 | Pass | 4.21 | Pass
108 | 5.2 | 5.7 | 6.1 | PASS | 7.7 | Pass | 8.2 | Pass | 9.5 | Warning | 4.6 | Pass | 5.9 |  | 3.8 |  | 5.6 | Pass | 4.19 | Pass | 4.51 | Pass | 9999 | Fail |  |  |  | 4.16 | Pass | 4.22 | Pass
109 | 5.4 | 5 | 6.1 | PASS | 7.2 | Pass | 8.3 | Pass | 7.5 | Pass | 4 | Pass | 5.4 |  | 6 |  | 4 | Pass | 4.1 | Pass | 6.25 | Pass | 9999 | Fail |  |  |  | 4.29 | Pass | 4.06 | Pass
110 | 5.4 | 6.3 | 5.5 | PASS | 9.8 | Warning | 8.5 | Pass | 11.6 | Warning | 4.2 | Pass | 4.3 |  | 5.4 |  | 4 | Pass | 5.81 | Pass | 6.44 | Pass | 7.27 | Pass |  |  |  | 5.33 | Pass | 4.21 | Pass
111 | 5.6 | 5.2 | 7 | PASS | 7.1 | Pass | 7.5 | Pass | 8.7 | Pass | 5.3 | Pass | 3.9 |  | 4.2 |  | 4.1 | Pass | 4.07 | Pass | 5.45 | Pass | 9999 | Fail |  |  |  | 4.18 | Pass | 4.27 | Pass
112 | 5.2 | 5.7 | 5.7 | PASS | 7.9 | Pass | 11 | Warning | 9.5 | Warning | 5.6 | Pass | 4.9 |  | 4 |  | 4.1 | Pass | 3.97 | Pass | 5.48 | Pass | 14 | Fail |  |  |  | 4.14 | Pass | 4.18 | Pass
113 | 6.2 | 5.3 | 6.2 | PASS | 7.3 | Pass | 9 | Warning | 9.3 | Warning | 4.6 | Pass | 5 |  | 4.3 |  | 4 | Pass | 4 | Pass | 5.46 | Pass | 9999 | Fail |  |  |  | 4.96 | Pass | 4.01 | Pass
114 | 5.6 | 6 | 5.8 | PASS | 7.5 | Pass | 7.8 | Pass | 9.4 | Warning | 4 | Pass | 4.6 |  | 4.9 |  | 4.2 | Pass | 4.17 | Pass | 4.85 | Pass | 9999 | Fail |  |  |  | 4.55 | Pass | 5.78 | Pass
115 | 6.2 | 6.2 | 6.4 | PASS | 9.7 | Warning | 7.8 | Pass | 12 | Failed | 4.3 | Pass | 5.3 |  | 4.2 |  | 4 | Pass | 4.02 | Pass | 5.49 | Pass | 4.39 | Pass |  |  |  | 5.1 | Pass | 5.96 | Pass
116 | 5.7 | 6 | 7.4 | PASS | 8.2 | Pass | 8 | Pass | 9.9 | Warning | 4.6 | Pass | 5.3 |  | 4.3 |  | 4 | Pass | 4.11 | Pass | 5.84 | Pass | 4.01 | Pass |  |  |  | 5.37 | Pass | 6.66 | Pass
117 | 5.9 | 5.1 | 6.1 | PASS | 7.2 | Pass | 7.5 | Pass | 8.5 | Pass | 4.5 | Pass | 6.8 |  | 12.1 | Fail | 4.4 | Pass | 4.33 | Pass | 6.52 | Pass | 4.13 | Pass |  |  |  | 4.98 | Pass | 6.75 | Pass
118 | 5.6 | 5.1 | 5.5 | PASS | 6.7 | Pass | 7.6 | Pass | 8.1 | Pass | 4.2 | Pass | 5.2 |  | 4.1 |  | 3.9 | Pass | 3.99 | Pass | 5.08 | Pass | 4.13 | Pass |  |  |  | 10.31 | Warning | 5.44 | Pass
119 | 5.9 | 6.1 | 5.5 | PASS | 7.6 | Pass | 8.5 | Pass | 8.2 | Pass | 4.8 | Pass | 14.5 | Fail | 4.2 |  | 3.9 | Pass | 4.02 | Pass | 9999 | Fail | 4.36 | Pass |  |  |  | 4.56 | Pass | 12.32 | Fail
120 | 5.4 | 5 | 6 | PASS | 6.4 | Pass | 8.5 | Pass | 7.9 | Pass | 6.3 | Pass | 4.7 |  | 4.1 |  | 3.7 | Pass | 4.16 | Pass | 5.14 | Pass | 4.13 | Pass |  |  |  | 4.15 | Pass | 5.75 | Pass
[21 empty] | 0.38333 | 38% BATTERY FAILED | 93 | Pass |  |  |  | 118 | Pass | 116 | Pass
[23 empty] | 3 | Warning |  |  |  | 1 | Warning | 0 | Warning
[23 empty] | 24 | Fail |  |  |  | 1 | Fail | 4 | Fail
[23 empty] | 27 | Non-Healthy Batteries |  |  |  | 2 | Non-Healthy Batteries | 4 | Non-Healthy Batteries

## MBE
Battery Spec: 12 Volts 120 AH
Brand:
Brand:
Sr. No. | 2017-07-20 | 16/11/2017 | Comments | 2018-05-02 | Comments | 2018-07-08 | Comments | 24/10/2018 | Comments - 24/10/2018 | 21/1/2019 | Comments - 21/1/2019 | 19/8/2019 | Comments - 19/8/2019 | 27/9/2019 | Comments - 27/9/2019 | 31/10/2019 | Comments - 31/10/2019 | 27/11/2019 | Comments - 27/11/2019 | 2020-01-10 | Comments - 10/1/2020 | 17/2/2020 | Comments - 17/2/2020 | 2020-11-12 | Comments - 11/12/2020 | 17/2/2021 | Comments - 17/2/2021 | 18/3/2021 | Comments - 18/3/2021 | 22/4/2021 | Comments - 22/4/2021
1 | 6 | 5.8 |  | 4.7 |  | 6 | Pass | 5.1 | Pass | 4.5 | Pass | 5.8 | Pass | 5.5 | Pass | 5.7 | Pass | 5.8 | Pass | 5.66 | Pass | 5.51 | Pass | 6.14 | Pass | 6.37 | Pass | 6.36 | Pass | 7.2 | Pass
2 | 6.1 | 4.8 |  | 5 |  | 5.4 | Pass | 6.6 | Pass | 5.7 | Pass | 6.6 | Pass | 5.5 | Pass | 6.5 | Pass | 6.3 | Pass | 5.34 | Pass | 6.21 | Pass | 6.58 | Pass | 6.18 | Pass | 6.68 | Pass | 6.7 | Pass
3 | 6.5 | 5.6 |  | 5.2 |  | 5.7 | Pass | 5.3 | Pass | 4.9 | Pass | 6 | Pass | 6.4 | Pass | 6.1 | Pass | 5.5 | Pass | 5.51 | Pass | 5.64 | Pass | 6.94 | Pass | 6.51 | Pass | 6.41 | Pass | 6.2 | Pass
4 | 5.9 | 4.1 |  | 4.4 |  | 4.6 | Pass | 5.6 | Pass | 6.2 | Pass | 5.9 | Pass | 5.1 | Pass | 5.6 | Pass | 6.1 | Pass | 5.83 | Pass | 5.95 | Pass | 5.94 | Pass | 6.37 | Pass | 6.7 | Pass | 6.2 | Pass
5 | 6 | 5.1 |  | 4.6 |  | 5.1 | Pass | 4.9 | Pass | 5.4 | Pass | 5.5 | Pass | 5.4 | Pass | 5.6 | Pass | 5.8 | Pass | 5.74 | Pass | 5.78 | Pass | 6.09 | Pass | 6.43 | Pass | 6.89 | Pass | 7.5 | Pass
6 | 6.1 | 4.2 |  | 5.9 |  | 4.6 | Pass | 4.7 | Pass | 6.3 | Pass | 5.7 | Pass | 5.1 | Pass | 5.2 | Pass | 6.9 | Pass | 6.4 | Pass | 4.92 | Pass | 5.47 | Pass | 6.81 | Pass | 5.95 | Pass | 6.8 | Pass
7 | 5.5 | 6.4 |  | 4.3 |  | 4.3 | Pass | 5.3 | Pass | 5.7 | Pass | 5.8 | Pass | 4.9 | Pass | 5.1 | Pass | 5 | Pass | 5.77 | Pass | 5.63 | Pass | 6.34 | Pass | 6.17 | Pass | 6.28 | Pass | 6.5 | Pass
8 | 6.2 | 4.7 |  | 6 |  | 4.5 | Pass | 6.2 | Pass | 5 | Pass | 7.4 | Pass | 6.5 | Pass | 6.3 | Pass | 5.5 | Pass | 5.31 | Pass | 4.9 | Pass | 5.86 | Pass | 6.35 | Pass | 6.22 | Pass | 6.7 | Pass
9 | 6.3 | 6.4 |  | 5.9 |  | 6.6 | Pass | 5.8 | Pass | 6.1 | Pass | 5.2 | Pass | 5.9 | Pass | 6.2 | Pass | 6.6 | Pass | 5.78 | Pass | 6.15 | Pass | 6.5 | Pass | 6.15 | Pass | 6.26 | Pass | 7.1 | Pass
10 | 6.1 | 6.6 |  | 4.5 |  | 4.4 | Pass | 5 | Pass | 5.3 | Pass | 6.9 | Pass | 6.4 | Pass | 6.6 | Pass | 5.5 | Pass | 5.35 | Pass | 5.59 | Pass | 5.91 | Pass | 6.77 | Pass | 6.26 | Pass | 6.5 | Pass
11 | 6.2 | 4.5 |  | 4.5 |  | 4.2 | Pass | 6.1 | Pass | 4.7 | Pass | 7.2 | Pass | 6.2 | Pass | 7.4 | Pass | 5.6 | Pass | 5.4 | Pass | 5.37 | Pass | 5.87 | Pass | 6.08 | Pass | 6.13 | Pass | 6.4 | Pass
12 | 6.1 | 5.4 |  | 5.6 |  | 5 | Pass | 5.6 | Pass | 6.2 | Pass | 5.6 | Pass | 5.7 | Pass | 5.3 | Pass | 6.4 | Pass | 5.55 | Pass | 5.55 | Pass | 6.49 | Pass | 6.61 | Pass | 6.23 | Pass | 7.4 | Pass
13 | 5.8 | 5.6 |  | 4.1 |  | 4.7 | Pass | 5.6 | Pass | 4.7 | Pass | 5.9 | Pass | 6.3 | Pass | 6.4 | Pass | 5.2 | Pass | 5.21 | Pass | 5.11 | Pass | 5.99 | Pass | 5.94 | Pass | 5.91 | Pass | 5.9 | Pass
14 | 6.2 | 4.5 |  | 5 |  | 4.7 | Pass | 5.4 | Pass | 6.6 | Pass | 6.3 | Pass | 5.7 | Pass | 5.1 | Pass | 5.7 | Pass | 6.19 | Pass | 5.48 | Pass | 5.81 | Pass | 6.71 | Pass | 6.91 | Pass | 6 | Pass
15 | 6.2 | 5.1 |  | 4.3 |  | 4.7 | Pass | 5.2 | Pass | 5.8 | Pass | 5.7 | Pass | 5 | Pass | 5.4 | Pass | 5.2 | Pass | 6.4 | Pass | 6.21 | Pass | 5.65 | Pass | 6.37 | Pass | 6.74 | Pass | 7 | Pass
16 | 6.4 | 5.4 |  | 4.3 |  | 4.7 | Pass | 6.2 | Pass | 5.2 | Pass | 5.8 | Pass | 5.2 | Pass | 5.6 | Pass | 5.3 | Pass | 6.37 | Pass | 6.28 | Pass | 5.81 | Pass | 6.51 | Pass | 6.41 | Pass | 6.9 | Pass
17 | 6.4 | 5.6 |  | 4.8 |  | 4.6 | Pass | 7.9 | Pass | 8 | Pass | 7 | Pass | 6.2 | Pass | 5.2 | Pass | 6.4 | Pass | 8.1 | Pass | 4.96 | Pass | 6.49 | Pass | 9.17 | Warning | 7.81 | Pass | 9.3 | Pass
18 | 6.4 | 5.1 |  | 4.6 |  | 4.8 | Pass | 6.2 | Pass | 4.7 | Pass | 5 | Pass | 5.8 | Pass | 5 | Pass | 5.3 | Pass | 5.32 | Pass | 5.27 | Pass | 5.48 | Pass | 5.63 | Pass | 5.69 | Pass | 6.3 | Pass
19 | 6.2 | 6.2 |  | 6.2 |  | 6.5 | Pass | 5.5 | Pass | 5.9 | Pass | 6.6 | Pass | 7.1 | Pass | 6.3 | Pass | 6.2 | Pass | 5.4 | Pass | 5.34 | Pass | 6.05 | Pass | 6.25 | Pass | 6.71 | Pass | 6.4 | Pass
20 | 6.8 | 4.7 |  | 4.4 |  | 5.5 | Pass | 5.8 | Pass | 4.7 | Pass | 5.4 | Pass | 5.4 | Pass | 4.8 | Pass | 5.2 | Pass | 5.46 | Pass | 5.21 | Pass | 5.79 | Pass | 5.91 | Pass | 5.96 | Pass | 6.7 | Pass
21 | 6.1 | 4.7 |  | 4.9 |  | 5 | Pass | 5.3 | Pass | 5.6 | Pass | 6 | Pass | 6 | Pass | 5.4 | Pass | 6.2 | Pass | 6.25 | Pass | 5.5 | Pass | 6.85 | Pass | 6.96 | Pass | 6.51 | Pass | 7.5 | Pass
22 | 7 |  | Reading did not come |  | Reading did not come | 5.2 | Pass | 5.5 | Pass | 5.6 | Pass | 5.7 | Pass | 5.1 | Pass | 5.3 | Pass | 5.9 | Pass | 3.9 | Pass | 5.46 | Pass | 4.88 | Pass | 5.04 | Pass | 5.23 | Pass | 6.1 | Pass
23 | 6.2 | 4.7 |  | 5.1 |  | 5.3 | Pass | 8.1 | Pass | 5.4 | Pass | 6.3 | Pass | 5.2 | Pass | 5.3 | Pass | 5.3 | Pass | 5.25 | Pass | 5.91 | Pass | 5.88 | Pass | 6.64 | Pass | 6.25 | Pass | 6.3 | Pass
24 | 6.1 | 5.3 |  | 4.4 |  | 4.6 | Pass | 5.3 | Pass | 5.9 | Pass | 6 | Pass | 5.2 | Pass | 5.6 | Pass | 5.4 | Pass | 5.69 | Pass | 5.71 | Pass | 5.82 | Pass | 6.87 | Pass | 6.8 | Pass | 6.8 | Pass
25 | 6.1 | 4.5 |  | 4.3 |  | 4.7 | Pass | 5.7 | Pass | 5.8 | Pass | 5.9 | Pass | 5.3 | Pass | 5.5 | Pass | 5.5 | Pass | 5.98 | Pass | 5.06 | Pass | 5.96 | Pass | 6.73 | Pass | 6.72 | Pass | 7.2 | Pass
26 | 5.9 | 4.7 |  | 4.6 |  | 4.8 | Pass | 5 | Pass | 5.4 | Pass | 5.5 | Pass | 5.1 | Pass | 5.8 | Pass | 5.1 | Pass | 6.09 | Pass | 5.22 | Pass | 5.93 | Pass | 6.96 | Pass | 6.61 | Pass | 6.9 | Pass
27 | 6 | 4.6 |  | 4.1 |  | 4.2 | Pass | 5.4 | Pass | 20.5 | Fail | 5.9 | Pass | 5.3 | Pass | 5.1 | Pass | 5.4 | Pass | 5.5 | Pass | 5.38 | Pass | 5.81 | Pass | 6.58 | Pass | 6.29 | Pass | 7 | Pass
28 | 6.1 | 4.2 |  | 4.4 |  | 4.7 | Pass | 5.2 | Pass | 4.9 | Pass | 5.7 | Pass | 5.6 | Pass | 5.5 | Pass | 5.2 | Pass | 6.19 | Pass | 5.39 | Pass | 6.09 | Pass | 6.15 | Pass | 6.13 | Pass | 7.5 | Pass
29 | 6.3 | 4.8 |  | 4.2 |  | 4.8 | Pass | 5.3 | Pass | 5.2 | Pass | 5.8 | Pass | 5.7 | Pass | 5.2 | Pass | 5.3 | Pass | 5.25 | Pass | 6.67 | Pass | 5.75 | Pass | 5.97 | Pass | 6.06 | Pass | 7.5 | Pass
30 | 5.5 | 5 |  | 4.7 |  | 5.2 | Pass | 5.5 | Pass | 5.1 | Pass | 5.9 | Pass | 5.9 | Pass | 5.1 | Pass | 5.5 | Pass | 5.3 | Pass | 4.97 | Pass | 5.81 | Pass | 6.56 | Pass | 6.05 | Pass | 6.1 | Pass
31 | 14.2 | 4.6 | Changed in Oct' 17 | 4.5 |  | 5.5 | Pass | 5.1 | Pass | 4.7 | Pass | 5.5 | Pass | 5.8 | Pass | 5.4 | Pass | 5.2 | Pass | 5.8 | Pass | 5.87 | Pass | 6.21 | Pass | 6.35 | Pass | 5.9 | Pass | 6.4 | Pass
32 | 6 | 5 |  | 4.3 |  | 4.7 | Pass | 5.6 | Pass | 29.1 | Fail | 5.5 | Pass | 6.4 | Pass | 5.3 | Pass | 5.5 | Pass | 5.38 | Pass | 5.23 | Pass | 6.23 | Pass | 6.88 | Pass | 6.41 | Pass | 7.3 | Pass
33 | 6.3 | 4.3 |  | 4.3 |  | 4.7 | Pass | 5.9 | Pass | 5.7 | Pass | 6.1 | Pass | 5.4 | Pass | 6.1 | Pass | 5.7 | Pass | 6.32 | Pass | 5.56 | Pass | 5.93 | Pass | 6.97 | Pass | 6.2 | Pass | 7 | Pass
34 | 6.1 | 4.6 |  | 4.3 |  | 4.7 | Pass | 5.2 | Pass | 5.6 | Pass | 6 | Pass | 5.2 | Pass | 5.6 | Pass | 5.3 | Pass | 5.91 | Pass | 6.35 | Pass | 6.54 | Pass | 7.06 | Pass | 6.91 | Pass | 8.4 | Pass
35 | 6.1 | 5.3 |  | 4.3 |  | 4.5 | Pass | 5.3 | Pass | 6 | Pass | 5.7 | Pass | 5.3 | Pass | 5.4 | Pass | 5.3 | Pass | 5.6 | Pass | 5.13 | Pass | 5.76 | Pass | 6.1 | Pass | 6.43 | Pass | 6.7 | Pass
36 | 6.3 | 4.3 |  | 4.3 |  | 4.7 | Pass | 5.3 | Pass | 5.5 | Pass | 6 | Pass | 5 | Pass | 5.7 | Pass | 5.2 | Pass | 5.81 | Pass | 4.92 | Pass | 5.85 | Pass | 6.63 | Pass | 6.08 | Pass | 6.8 | Pass
37 | 6.1 | 4.7 |  | 4.2 |  | 4.5 | Pass | 5.6 | Pass | 5.5 | Pass | 5.5 | Pass | 5.3 | Pass | 5.1 | Pass | 5.4 | Pass | 5.49 | Pass | 6.06 | Pass | 5.62 | Pass | 6.13 | Pass | 5.7 | Pass | 6.4 | Pass
38 | 6.2 | 4.4 |  | 4.4 |  | 4.7 | Pass | 5.2 | Pass | 4.7 | Pass | 5.9 | Pass | 5.1 | Pass | 5.5 | Pass | 5.3 | Pass | 5.99 | Pass | 5.47 | Pass | 5.9 | Pass | 6.46 | Pass | 6.07 | Pass | 6.8 | Pass
39 | 5.9 | 4.8 |  | 4.7 |  | 5 | Pass | 5.3 | Pass | 5 | Pass | 5.7 | Pass | 5.2 | Pass | 5.3 | Pass | 5.3 | Pass | 5.34 | Pass | 5.88 | Pass | 6.52 | Pass | 6.18 | Pass | 6.25 | Pass | 7 | Pass
40 | 6.3 | 3.9 |  | 4.6 |  | 5.3 | Pass | 4.1 | Pass | 4.4 | Pass | 4.8 | Pass | 4.1 | Pass | 5.3 | Pass | 4 | Pass | 5.21 | Pass | 5.78 | Pass | 6.39 | Pass | 5.96 | Pass | 6.08 | Pass | 6.5 | Pass
41 | 4.5 | 3.7 |  | 4.1 |  | 4.2 | Pass | 4 | Pass | 3.9 | Pass | 4.8 | Pass | 4.7 | Pass | 4.4 | Pass | 4.1 | Pass | 4.24 | Pass | 6.51 | Pass | 7.77 | Pass | 9.09 | Warning | 9.49 | Warning | 11 | Warning
42 | 4.6 | 3.9 |  | 3.9 |  | 4 | Pass | 4.3 | Pass | 3.9 | Pass | 4.6 | Pass | 4.7 | Pass | 4.5 | Pass | 4.2 | Pass | 4.91 | Pass | 6.03 | Pass | 9.05 | Warning | 10.47 | Warning | 10.89 | Warning | 12.6 | Fail
43 | 4.8 | 3.8 |  | 4 |  | 4 | Pass | 4.2 | Pass | 4.1 | Pass | 4.5 | Pass | 4.3 | Pass | 4.7 | Pass | 4.1 | Pass | 5.11 | Pass | 6.27 | Pass | 9.7 | Warning | 11.43 | Warning | 11.52 | Warning | 13.8 | Fail
44 | 4.8 | 3.9 |  | 3.4 |  | 3.9 | Pass | 4 | Pass | 4.5 | Pass | 4.5 | Pass | 3.9 | Pass | 4.5 | Pass | 4 | Pass | 4.72 | Pass | 6.13 | Pass | 7.89 | Pass | 9.43 | Warning | 10.08 | Warning | 11.2 | Warning
45 | 4.7 | 3.4 |  | 3.3 |  | 3.9 | Pass | 4.2 | Pass | 4.2 | Pass | 4.7 | Pass | 4.3 | Pass | 4.3 | Pass | 4.3 | Pass | 4.55 | Pass | 6.09 | Pass | 7.95 | Pass | 9.38 | Warning | 9.86 | Warning | 11.2 | Warning
46 | 4.4 | 3.7 |  | 3.4 |  | 4 | Pass | 4.3 | Pass | 4.4 | Pass | 4.4 | Pass | 4.6 | Pass | 4.7 | Pass | 4.1 | Pass | 5.16 | Pass | 5.35 | Pass | 10.84 | Warning | 13.08 | Fail | 13.79 | Fail | 15.4 | Fail
47 | 4.7 | 3.4 |  | 3.4 |  | 3.7 | Pass | 3.8 | Pass | 4.2 | Pass | 4.5 | Pass | 4.6 | Pass | 4.6 | Pass | 4.3 | Pass | 5.15 | Pass | 6.12 | Pass | 9.07 | Warning | 10.3 | Warning | 10.84 | Warning | 12.1 | Warning
48 | 4.6 | 3.6 |  | 3.6 |  | 4.3 | Pass | 4.3 | Pass | 4.2 | Pass | 4.4 | Pass | 4.6 | Pass | 4.7 | Pass | 4.6 | Pass | 4.57 | Pass | 5.5 | Pass | 12.68 | Fail | 15.28 | Fail | 16.12 | Fail | 19.8 | Fail
49 | 4.7 | 3.5 |  | 3.9 |  | 3.8 | Pass | 4.7 | Pass | 4.4 | Pass | 4.5 | Pass | 5.7 | Pass | 4.8 | Pass | 5.5 | Pass | 4.56 | Pass | 5.69 | Pass | 9.55 | Warning | 11.4 | Warning | 12.14 | Fail | 13.6 | Warning
50 | 4.5 | 4.2 |  | 4.1 |  | 4.3 | Pass | 4.2 | Pass | 4.7 | Pass | 5 | Pass | 4.5 | Pass | 4.4 | Pass | 4.3 | Pass | 5.94 | Pass | 5.37 | Pass | 28.64 | Fail | 9999 | Fail | 9999 | Fail | 51.8 | Fail
51 | 4.5 | 4 |  | 4 |  | 4.2 | Pass | 3.9 | Pass | 4.2 | Pass | 4.6 | Pass | 4.8 | Pass | 4.9 | Pass | 4.7 | Pass | 5.04 | Pass | 7.65 | Pass | 7.56 | Pass | 8.85 | Pass | 9.35 | Warning | 10.9 | Warning
52 | 4.6 | 4 |  | 3.8 |  | 3.7 | Pass | 4.4 | Pass | 4.2 | Pass | 4.8 | Pass | 5 | Pass | 5 | Pass | 4.9 | Pass | 5.39 | Pass | 5.45 | Pass | 15.69 | Fail | 20.17 | Fail | 24.98 | Fail | 27.9 | Fail
53 | 4.5 | 3.4 |  | 3.9 |  | 4 | Pass | 4.5 | Pass | 4.5 | Pass | 4.9 | Pass | 5.2 | Pass | 4.7 | Pass | 5 | Pass | 5.43 | Pass | 5.77 | Pass | 13 | Fail | 16.64 | Fail | 17.4 | Fail | 19.6 | Fail
54 | 4.7 | 3.8 |  | 3.4 |  | 3.6 | Pass | 3.9 | Pass | 4.6 | Pass | 4.8 | Pass | 4.7 | Pass | 4.4 | Pass | 4.8 | Pass | 5.3 | Pass | 6.2 | Pass | 13.34 | Fail | 16.37 | Fail | 17.42 | Fail | 19.3 | Fail
55 | 4.8 | 3.8 |  | 3.4 |  | 3.7 | Pass | 4.5 | Pass | 4.3 | Pass | 4.6 | Pass | 7.8 | Pass | 7.8 | Pass | 8.3 | Pass | 4.69 | Pass | 5.88 | Pass | 9.09 | Warning | 10.97 | Warning | 11.13 | Warning | 12.7 | Fail
56 | 4.8 | 3.8 |  | 3.5 |  | 3.8 | Pass | 4.2 | Pass | 4.6 | Pass | 6.6 | Pass | 4.8 | Pass | 5.6 | Pass | 4.4 | Pass | 8.98 | Pass | 5.84 | Pass | 9999 | Fail | 9999 | Fail | 9999 | Fail | 49.4 | Fail
57 | 4.6 | 3.9 |  | 3.7 |  | 3.9 | Pass | 4 | Pass | 4.2 | Pass | 4.6 | Pass | 4.7 | Pass | 4.7 | Pass | 4.4 | Pass | 5.12 | Pass | 5.81 | Pass | 14.16 | Fail | 18.52 | Fail | 20.1 | Fail | 23.2 | Fail
58 | 4.9 | 3.5 |  | 3.6 |  | 4.2 | Pass | 4.1 | Pass | 4 | Pass | 5 | Pass | 4.9 | Pass | 4.9 | Pass | 5 | Pass | 4.74 | Pass | 5.53 | Pass | 8.63 | Pass | 10.59 | Warning | 10.91 | Warning | 12.5 | Fail
59 | 4.6 | 3.5 |  | 4.2 |  | 4.1 | Pass | 4.2 | Pass | 4.2 | Pass | 4.8 | Pass | 4.7 | Pass | 4.9 | Pass | 4.6 | Pass | 5.35 | Pass | 6.65 | Pass | 17.95 | Fail | 19.55 | Fail | 21.55 | Fail | 25.5 | Fail
60 | 4.6 | 3.8 |  | 3.9 |  | 4.3 | Pass | 4.1 | Pass | 4.1 | Pass | 4.5 | Pass | 4.5 | Pass | 4.7 | Pass | 4.8 | Pass | 4.17 | Pass | 5.65 | Pass | 7.53 | Pass | 8.44 | Pass | 8.75 | Pass | 9.5 | Warning
61 | 4.6 | 3.4 |  | 4 |  | 4.3 | Pass | 4.2 | Pass | 3.6 | Pass | 4.3 | Pass | 4.6 | Pass | 4.8 | Pass | 4.8 | Pass | 4.99 | Pass | 5.86 | Pass | 9.23 | Fail | 10.56 | Warning | 11.1 | Warning | 12 | Warning
62 | 4.9 | 3.9 |  | 3.4 |  | 4 | Pass | 4.2 | Pass | 4.3 | Pass | 4.6 | Pass | 4.7 | Pass | 4.9 | Pass | 4.9 | Pass | 4.84 | Pass | 6.13 | Pass | 7.84 | Pass | 8.82 | Pass | 9.15 | Warning | 10.6 | Warning
63 | 4.8 | 3.8 |  | 3.3 |  | 4.1 | Pass | 3.9 | Pass | 4.3 | Pass | 4.6 | Pass | 4.5 | Pass | 4.4 | Pass | 4.8 | Pass | 5.05 | Pass | 6.06 | Pass | 9.98 | Fail | 11.21 | Warning | 11.74 | Warning | 12.9 | Fail
64 | 4.6 | 3.4 |  | 3.3 |  | 3.8 | Pass | 3.9 | Pass | 4.5 | Pass | 4.7 | Pass | 4.6 | Pass | 4.6 | Pass | 4.2 | Pass | 4.57 | Pass | 5.49 | Pass | 7.49 | Pass | 9.09 | Warning | 8.95 | Pass | 10.3 | Warning
65 | 4.8 | 4.1 |  | 3.3 |  | 4.3 | Pass | 4.3 | Pass | 4.2 | Pass | 6.6 | Pass | 4.7 | Pass | 4.8 | Pass | 4.4 | Pass | 4.74 | Pass | 5.9 | Pass | 10.17 | Fail | 12.44 | Fail | 12.99 | Fail | 14.8 | Fail
66 | 4.7 | 3.6 |  | 3.4 |  | 4 | Pass | 4 | Pass | 4.2 | Pass | 4.6 | Pass | 4.5 | Pass | 4.6 | Pass | 4.5 | Pass | 4.37 | Pass | 5.24 | Pass | 7.44 | Pass | 8.97 | Pass | 9.1 | Warning | 10.9 | Warning
67 | 4.9 | 3.9 |  | 3.3 |  | 4.2 | Pass | 4.4 | Pass | 4.3 | Pass | 4.5 | Pass | 4.5 | Pass | 4.6 | Pass | 4.6 | Pass | 4.68 | Pass | 6.3 | Pass | 6.89 | Pass | 8.62 | Pass | 8.67 | Pass | 9.9 | Warning
68 | 4.8 | 3.9 |  | 3.8 |  | 4.2 | Pass | 4 | Pass | 4.3 | Pass | 4.6 | Pass | 4.6 | Pass | 4.1 | Pass | 4.8 | Pass | 4.71 | Pass | 5.87 | Pass | 7.02 | Pass | 8.23 | Pass | 8.19 | Pass | 9.3 | Warning
69 | 4.4 | 3.7 |  | 3.4 |  | 4.1 | Pass | 4 | Pass | 4.1 | Pass | 4.7 | Pass | 4.7 | Pass | 4 | Pass | 5 | Pass | 4.99 | Pass | 5.64 | Pass | 8.94 | Pass | 10.14 | Warning | 10.04 | Warning | 12.1 | Fail
70 | 4.3 | 3.8 |  | 4.1 |  | 3.9 | Pass | 4 | Pass | 4.3 | Pass | 4.7 | Pass | 5.2 | Pass | 5.4 | Pass | 5.4 | Pass | 4.71 | Pass | 5.8 | Pass | 8.59 | Pass | 9.97 | Warning | 9.75 | Warning | 11 | Warning
71 | 4.7 | 3.8 |  | 3.9 |  | 3.9 | Pass | 4.1 | Pass | 4.4 | Pass | 4.6 | Pass | 4.7 | Pass | 4.7 | Pass | 4.9 | Pass | 5.53 | Pass | 5.56 | Pass | 17.59 | Fail | 24.54 | Fail | 24.98 | Fail | 32.6 | Fail
72 | 4.7 | 4 |  | 3.5 |  | 4.1 | Pass | 3.9 | Pass | 4.2 | Pass | 4.6 | Pass | 4.8 | Pass | 4.8 | Pass | 4.3 | Pass | 4.91 | Pass | 5.91 | Pass | 12.49 | Fail | 15.75 | Fail | 17.47 | Fail | 19.9 | Fail
73 | 4.6 | 4.2 |  | 3.4 |  | 4.4 | Pass | 4 | Pass | 4.3 | Pass | 4.5 | Pass | 5 | Pass | 5.8 | Pass | 5.4 | Pass | 4.83 | Pass | 5.71 | Pass | 9.32 | Warning | 10.96 | Warning | 11.39 | Warning | 12.6 | Fail
74 | 4.6 | 4 |  | 3.4 |  | 4.7 | Pass | 4.5 | Pass | 4.6 | Pass | 4.7 | Pass | 4.5 | Pass | 4.2 | Pass | 4.5 | Pass | 6.27 | Pass | 6.28 | Pass | 17.31 | Fail | 9999 | Fail | 9999 | Warning | 9999 | Fail
75 | 4.9 | 4.1 |  | 3.4 |  | 3.7 | Pass | 4 | Pass | 4.3 | Pass | 4.4 | Pass | 4.3 | Pass | 4.3 | Pass | 4.1 | Pass | 4.84 | Pass | 5.83 | Pass | 7.27 | Pass | 8.18 | Pass | 8.02 | Pass | 9.5 | Warning
76 | 4.7 | 4 |  | 3.3 |  | 3.5 | Pass | 4.4 | Pass | 4.4 | Pass | 4.5 | Pass | 4.6 | Pass | 4.9 | Pass | 4.8 | Pass | 4.37 | Pass | 5.44 | Pass | 7.48 | Pass | 8.78 | Pass | 9.45 | Warning | 10.5 | Warning
77 | 4.8 | 3.8 |  | 3.4 |  | 4 | Pass | 4.3 | Pass | 4.3 | Pass | 4.6 | Pass | 4.4 | Pass | 4.7 | Pass | 4.9 | Pass | 4.52 | Pass | 6.52 | Pass | 10.19 | Warning | 12.51 | Fail | 13.2 | Fail | 15.3 | Fail
78 | 4.9 | 3.6 |  | 3.9 |  | 4.4 | Pass | 4.1 | Pass | 4.4 | Pass | 4.7 | Pass | 4.9 | Pass | 5 | Pass | 4.5 | Pass | 4.71 | Pass | 5.4 | Pass | 11.31 | Warning | 14.67 | Fail | 15.33 | Fail | 18.6 | Fail
79 | 4.4 | 3.3 |  | 3.7 |  | 4.1 | Pass | 4.1 | Pass | 4.3 | Pass | 4.5 | Pass | 4.4 | Pass | 4.4 | Pass | 4.5 | Pass | 4.79 | Pass | 6.09 | Pass | 9.59 | Warning | 11.07 | Warning | 10.9 | Warning | 12.7 | Fail
80 | 4.2 | 3.5 |  | 3.7 |  | 4 | Pass | 4.5 | Pass | 4.1 | Pass | 4.3 | Pass | 4.7 | Pass | 4.8 | Pass | 4.9 | Pass | 4.77 | Pass | 5.82 | Pass | 8.69 | Pass | 10.24 | Warning | 10.55 | Warning | 11.7 | Warning
81 | 4.1 | 4.1 |  | 4.1 |  | 3.9 | Pass | 4.1 | Pass | 4.2 | Pass | 4.6 | Pass | 4.6 | Pass | 4.7 | Pass | 4.7 | Pass | 4.93 | Pass | 6.65 | Pass | 9.37 | Warning | 11.3 | Warning | 12.24 | Fail | 91.3 | Fail
82 | 4.9 | 4 |  | 3.7 |  | 4.5 | Pass | 4.1 | Pass | 4 | Pass | 4.6 | Pass | 4.8 | Pass | 5 | Pass | 5 | Pass | 4.91 | Pass | 6.94 | Pass | 9.13 | Warning | 10.69 | Warning | 11.57 | Warning | 13.1 | Fail
83 | 4.5 | 3.9 |  | 3.6 |  | 4 | Pass | 4.3 | Pass | 3.9 | Pass | 4.7 | Pass | 5.3 | Pass | 5.8 | Pass | 5.4 | Pass | 5.18 | Pass | 5.91 | Pass | 12.85 | Fail | 16.03 | Fail | 18.02 | Fail | 20.9 | Fail
84 | 4.7 | 3.5 |  | 3.7 |  | 4.2 | Pass | 3.9 | Pass | 4.7 | Pass | 5.2 | Pass | 4.7 | Pass | 4.8 | Pass | 5.8 | Pass | 5.8 | Pass | 6.56 | Pass | 9999 | Fail | 9999 | Fail | 9999 | Fail | 9999 | Fail
85 | 4.5 | 3.6 |  | 3.4 |  | 3.9 | Pass | 4.7 | Pass | 4.3 | Pass | 4.6 | Pass | 9.4 | Pass | 11.4 | Warning | 5.1 | Pass | 4.92 | Pass | 7.68 | Pass | 9.54 | Warning | 11.05 | Warning | 12.15 | Fail | 14.4 | Fail
86 | 4.7 | 3.6 |  | 3.3 |  | 3.9 | Pass | 3.6 | Pass | 5.1 | Pass | 8.7 | Pass | 4.7 | Pass | 5 | Pass | 12.8 | Fail | 16.09 | Fail | 6.52 | Pass | 4.04 | Pass | 5.17 | Pass | 4.83 | Pass | 4.8 | Pass
87 | 4.6 | 3.8 |  | 3.8 |  | 3.6 | Pass | 4 | Pass | 4.3 | Pass | 4.6 | Pass | 4.6 | Pass | 4.8 | Pass | 4.3 | Pass | 4.94 | Pass | 6.36 | Pass | 10.38 | Warning | 12.63 | Fail | 13.72 | Fail | 16.2 | Fail
88 | 4.5 | 3.2 |  | 3.9 |  | 4.2 | Pass | 4.2 | Pass | 4.5 | Pass | 4.6 | Pass | 4.9 | Pass | 5.1 | Pass | 4.4 | Pass | 5.27 | Pass | 9.64 | Warning | 11.73 | Warning | 15.45 | Fail | 18 | Fail | 21.2 | Fail
89 | 4.7 | 3.9 |  | 4.2 |  | 4 | Pass | 4.2 | Pass | 4.6 | Pass | 4.8 | Pass | 4.7 | Pass | 4.7 | Pass | 4.5 | Pass | 5.37 | Pass | 6.61 | Pass | 11.85 | Warning | 14.02 | Fail | 14.91 | Fail | 17.1 | Fail
90 | 4.7 | 3.9 |  | 3.4 |  | 4.2 | Pass | 4.3 | Pass | 3.6 | Pass | 4.5 | Pass | 5.1 | Pass | 5.4 | Pass | 4.2 | Pass | 4.27 | Pass | 6.05 | Pass | 8.56 | Pass | 10.71 | Warning | 11.03 | Warning | 12.7 | Fail
91 | 4.6 | 3.7 |  | 4.1 |  | 3.8 | Pass | 4.3 | Pass | 4.6 | Pass | 5.3 | Pass | 4.8 | Pass | 5.1 | Pass | 4.9 | Pass | 5.85 | Pass | 6.26 | Pass | 15.23 | Fail | 18.36 | Fail | 19.87 | Fail | 22.6 | Fail
92 | 4.4 | 3.8 |  | 3.7 |  | 4.3 | Pass | 4.3 | Pass | 4.6 | Pass | 5.1 | Pass | 5.1 | Pass | 5.2 | Pass | 5.3 | Pass | 5.5 | Pass | 6.52 | Pass | 13.61 | Fail | 16.71 | Fail | 18.57 | Fail | 21 | Fail
93 | 4.7 | 4 |  | 3.4 |  | 4.2 | Pass | 4.5 | Pass | 4.4 | Pass | 4.9 | Pass | 5.4 | Pass | 5.8 | Pass | 5.3 | Pass | 5.75 | Pass | 6.63 | Pass | 16.04 | Fail | 20.68 | Fail | 23.29 | Fail | 29.5 | Fail
94 | 4.6 | 4.5 |  | 4.3 |  | 4 | Pass | 5.6 | Pass | 4.6 | Pass | 4.9 | Pass | 6.1 | Pass | 6.3 | Pass | 5.6 | Pass | 5.97 | Pass | 6.42 | Pass | 16.34 | Fail | 21.1 | Fail | 22.75 | Fail | 26.4 | Fail
95 | 55.5 | 3.8 | Changed in Oct' 17 | 3.4 |  | 5.4 | Pass | 4 | Pass | 6.7 | Pass | 6.2 | Pass | 4.8 | Pass | 4.7 | Pass | 6.9 | Pass | 6.77 | Pass | 6 | Pass | 16.81 | Fail | 19.63 | Fail | 21.22 | Fail | 23.5 | Fail
96 | 4.6 | 3.7 |  | 3.5 |  | 3.8 | Pass | 3.7 | Pass | 4.1 | Pass | 4.8 | Pass | 5.1 | Pass | 4.9 | Pass | 4.6 | Pass | 4.75 | Pass | 6.81 | Pass | 8.84 | Pass | 10.54 | Warning | 11.51 | Warning | 12.8 | Fail
97 | 4.7 | 3.8 |  | 3.4 |  | 4.4 | Pass | 3.6 | Pass | 4.1 | Pass | 4.7 | Pass | 4.8 | Pass | 5.1 | Pass | 4.5 | Pass | 5.18 | Pass | 5.72 | Pass | 11.25 | Warning | 14.09 | Fail | 15.4 | Fail | 18 | Fail
98 | 4.7 | 4 |  | 3.9 |  | 4.2 | Pass | 4.2 | Pass | 4.1 | Pass | 4.8 | Pass | 4.7 | Pass | 4.7 | Pass | 5.2 | Pass | 4.78 | Pass | 5.7 | Pass | 13.42 | Fail | 16.85 | Fail | 18.5 | Fail | 32.9 | Fail
99 | 4.6 | 4 |  | 3.9 |  | 3.9 | Pass | 4.4 | Pass | 4.4 | Pass | 4.7 | Pass | 5 | Pass | 5.2 | Pass | 5.3 | Pass | 5.19 | Pass | 6.47 | Pass | 10.56 | Warning | 12.61 | Fail | 13.69 | Fail | 15.4 | Fail
100 | 4.4 | 3.8 |  | 3.4 |  | 3.5 | Pass | 4 | Pass | 4.6 | Pass | 5.3 | Pass | 4.4 | Pass | 4.8 | Pass | 5.3 | Pass | 4.81 | Pass | 7.26 | Pass | 19.39 | Fail | 25.71 | Fail | 30.18 | Fail | 41.4 | Fail
101 | 4.6 | 3.8 |  | 3.4 |  | 4.3 | Pass | 4.3 | Pass | 4.2 | Pass | 4.5 | Pass | 4.6 | Pass | 5.4 | Pass | 4.6 | Pass | 4.97 | Pass | 6.51 | Pass | 9.45 | Warning | 12.31 | Fail | 12.83 | Fail | 15.8 | Fail
102 | 4.7 | 4 |  | 3.4 |  | 4.3 | Pass | 4.1 | Pass | 4.6 | Pass | 4.9 | Pass | 4.6 | Pass | 4.7 | Pass | 4.6 | Pass | 5.33 | Pass | 6.26 | Pass | 9.59 | Warning | 11.97 | Warning | 12.66 | Fail | 14.1 | Fail
103 | 4.5 | 3.7 |  | 3.4 |  | 3.9 | Pass | 4.2 | Pass | 4.6 | Pass | 4.7 | Pass | 4.8 | Pass | 4.8 | Pass | 4.6 | Pass | 5.15 | Pass | 9.47 | Warning | 9.71 | Warning | 11.8 | Warning | 12.6 | Fail | 15.2 | Fail
104 | 4.6 | 4 |  | 3.5 |  | 4.3 | Pass | 4.2 | Pass | 4.2 | Pass | 5.1 | Pass | 4.7 | Pass | 4.4 | Pass | 6 | Pass | 5.73 | Pass | 6.37 | Pass | 17.35 | Fail | 22.45 | Fail | 26.92 | Fail | 31.1 | Fail
105 | 4.5 | 3.5 |  | 3.5 |  | 4.2 | Pass | 4.3 | Pass | 4.3 | Pass | 4.6 | Pass | 5 | Pass | 4.9 | Pass | 4.8 | Pass | 4.97 | Pass | 6.49 | Pass | 10.04 | Warning | 12.03 | Fail | 13.01 | Fail | 15.5 | Fail
106 | 4.4 | 3.8 |  | 3.4 |  | 4 | Pass | 4.3 | Pass | 4.5 | Pass | 4.8 | Pass | 4.9 | Pass | 4.4 | Pass | 4.8 | Pass | 5.68 | Pass | 6.89 | Pass | 13.35 | Fail | 9999 | Fail | 17.27 | Fail | 28.8 | Fail
107 | 4.6 | 3.8 |  | 3.6 |  | 4.3 | Pass | 3.9 | Pass | 4.4 | Pass | 4.8 | Pass | 4.5 | Pass | 4.7 | Pass | 5.1 | Pass | 5.49 | Pass | 7.57 | Pass | 11.4 | Warning | 14.19 | Fail | 15.21 | Fail | 17.8 | Fail
108 | 4.6 | 3.7 |  | 3.7 |  | 3.6 | Pass | 4 | Pass | 4.3 | Pass | 4.8 | Pass | 4.4 | Pass | 5 | Pass | 4.8 | Pass | 5.46 | Pass | 6.12 | Pass | 10.88 | Warning | 12.71 | Fail | 13.79 | Fail | 16.1 | Fail
109 | 4.5 | 3.6 |  | 3.3 |  | 3.4 | Pass | 4 | Pass | 4.1 | Pass | 4.5 | Pass | 4.5 | Pass | 5.2 | Pass | 4.7 | Pass | 4.62 | Pass | 7.44 | Pass | 8.32 | Pass | 9.93 | Warning | 10.57 | Warning | 12 | Warning
110 | 4.5 | 4.1 |  | 3.3 |  | 3.5 | Pass | 4.4 | Pass | 4.1 | Pass | 4.7 | Pass | 4.3 | Pass | 4.5 | Pass | 4.7 | Pass | 4.8 | Pass | 5.45 | Pass | 9.85 | Warning | 11.84 | Warning | 13.07 | Fail | 14.5 | Fail
111 | 4.7 | 3.9 |  | 3.4 |  | 4.5 | Pass | 4 | Pass | 4.4 | Pass | 4.8 | Pass | 4.5 | Pass | 5.1 | Pass | 4.2 | Pass | 4.94 | Pass | 6.84 | Pass | 7.58 | Pass | 8.31 | Pass | 9.4 | Pass | 10.4 | Warning
112 | 4.6 | 3.7 |  | 3.3 |  | 4.2 | Pass | 4.1 | Pass | 4.2 | Pass | 4.8 | Pass | 4.9 | Pass | 5.2 | Pass | 5.1 | Pass | 5.18 | Pass | 6.7 | Pass | 11.47 | Warning | 14.36 | Fail | 15.38 | Fail | 18.2 | Fail
113 | 4.5 | 4.1 |  | 3.1 |  | 4.4 | Pass | 4.4 | Pass | 4.3 | Pass | 5.1 | Pass | 4.9 | Pass | 4.5 | Pass | 4.9 | Pass | 5.45 | Pass | 5.63 | Pass | 9.16 | Warning | 10.73 | Warning | 11.34 | Warning | 12.9 | Fail
114 | 4.4 | 3.7 |  | 3.3 |  | 3.5 | Pass | 4.2 | Pass | 4.9 | Pass | 4.8 | Pass | 4.9 | Pass | 4.9 | Pass | 4.9 | Pass | 5.82 | Pass | 6.54 | Pass | 10.51 | Warning | 12.72 | Fail | 13.4 | Warning | 15.7 | Fail
115 | 4.5 | 4.1 |  | 3.4 |  | 3.5 | Pass | 3.7 | Pass | 4.4 | Pass | 5 | Pass | 5 | Pass | 4.8 | Pass | 4.7 | Pass | 4.83 | Pass | 6.19 | Pass | 14.18 | Fail | 18.38 | Fail | 20.99 | Fail | 24 | Fail
116 | 4.5 | 3.6 |  | 3.3 |  | 3.8 | Pass | 3.8 | Pass | 4.7 | Pass | 4.9 | Pass | 4.5 | Pass | 4.6 | Pass | 5 | Pass | 5.04 | Pass | 4.77 | Pass | 8.97 | Pass | 10.86 | Warning | 11.8 | Warning | 13.5 | Fail
117 | 4.5 | 4.1 |  | 3.4 |  | 3.6 | Pass | 4.1 | Pass | 4.1 | Pass | 4.8 | Pass | 4.7 | Pass | 4.8 | Pass | 4.9 | Pass | 4.7 | Pass | 5.62 | Pass | 10.4 | Warning | 13.05 | Fail | 14.77 | Fail | 18.1 | Fail
118 | 4.6 | 3.9 |  | 3.3 |  | 3.8 | Pass | 4.5 | Pass | 4.5 | Pass | 4.6 | Pass | 4.9 | Pass | 4.7 | Pass | 4.8 | Pass | 5.01 | Pass | 6.95 | Pass | 11.88 | Warning | 14.29 | Fail | 15.51 | Fail | 17.5 | Fail
119 | 4.5 | 3.6 |  | 3.4 |  | 4.1 | Pass | 4.3 | Pass | 4.2 | Pass | 4.6 | Pass | 4.6 | Pass | 4.9 | Pass | 4.9 | Pass | 5.08 | Pass | 6.57 | Pass | 11.07 | Warning | 13.93 | Fail | 14.82 | Fail | 17 | Fail
120 | 4.4 | 4.7 |  | 3.4 |  | 3.5 | Pass | 3.9 | Pass |  | Not Determined |  | Not Determined |  | Not Determined |  | Not Determined | 4.9 | Pass | 4.71 | Pass | 5.69 | Pass | 12.12 | Fail | 14.69 | Fail | 16.11 | Fail | 18.3 | Fail
[24 empty] | 62 | Pass | 49 | Pass | 46 | Pass | 40 | Pass
[24 empty] | 34 | Warning | 29 | Warning | 26 | Warning | 18 | Warning
[24 empty] | 24 | Fail | 42 | Fail | 48 | Fail | 62 | Fail
[24 empty] | 58 | Non-Healthy Batteries | 71 | Non-Healthy Batteries | 74 | Non-Healthy Batteries | 80 | Non-Healthy Batteries

## NCPRE
Battery Spec: 12 Volts, 120 AH
Brand:
Brand:
Sr. No. | 2017-07-20 | 30/8/2017 | 16/11/2017 | Comments | 2018-01-02 | Comments | 2018-07-08 | Comments | 21/1/2019 | Comments - 21/1/2019 | 19/8/2019 | Comments - 19/8/2019 | 27/9/2019 | Comments - 27/9/2019 | 31/10/2019 | Comments - 31/10/2019 | 29/11/2019 | Comments - 29/11/2019 | 2020-11-12 | Comments - 11/12/2020 | 17/2/2021 | Comments - 17/2/2021 | 18/3/2021 | Comments - 18/3/2021 | 22/4/2021 | Comments - 22/4/2021
1 | 4.2 | 4.2 | 5.8 |  | 4.5 |  | 4.5 | Pass | 4.4 | Pass | 4.7 | Pass | 5.1 | Pass | 5.9 |  | 4.6 | Pass | 8.7 | Pass | 5.72 | Pass | 5.43 | Pass | 7.1 | Pass
2 | 6.5 | 4.4 | 4.8 |  | 4.6 |  | 5.4 | Pass | 5.1 | Pass | 5.3 | Pass | 4.3 | Pass | 5.6 |  | 4.8 | Pass | 7.48 | Pass | 5.9 | Pass | 5.79 | Pass | 6 | Pass
3 | 5.1 | 4.5 | 5.6 |  | 4.3 |  | 4.4 | Pass | 4.8 | Pass | 5.5 | Pass | 4.6 | Pass | 7.2 |  | 5.5 | Pass | 11.09 | Warning | 6.3 | Pass | 6.15 | Pass | 6.7 | Pass
4 | 4.3 | 4.5 | 4.1 |  | 4.3 |  | 4.2 | Pass | 4.1 | Pass | 5.1 | Pass | 4.9 | Pass | 5.2 |  | 4.2 | Pass | 6.84 | Pass | 5.28 | Pass | 4.89 | Pass | 6.9 | Pass
5 | 4.5 | 4.7 | 5.1 |  | 4.4 |  | 4.2 | Pass | 4.6 | Pass | 5.6 | Pass | 4.2 | Pass | 5.6 |  | 5.2 | Pass | 7.64 | Pass | 6.92 | Pass | 6.23 | Pass | 7.4 | Pass
6 | 4.2 | 4.1 | 4.2 |  | 4.3 |  | 4 | Pass | 4.4 | Pass | 5.4 | Pass | 5 | Pass | 5.2 |  | 4.8 | Pass | 10 | Warning | 5.96 | Pass | 5.76 | Pass | 6.3 | Pass
7 | 4.2 | 4.4 | 6.4 |  | 4.3 |  | 4.1 | Pass | 4.2 | Pass | 5.1 | Pass | 4.7 | Pass | 6 |  | 4.7 | Pass | 9.61 | Warning | 7.54 | Pass | 5.92 | Pass | 7 | Pass
8 | 4.1 | 4.7 | 4.7 |  | 5.1 |  | 4.1 | Pass | 4.7 | Pass | 5.2 | Pass | 4.5 | Pass | 5.3 |  | 4.9 | Pass | 7.17 | Pass | 6.93 | Pass | 6.44 | Pass | 6.4 | Pass
9 | 4.5 | 4.1 | 6.4 |  | 4.4 |  | 5.1 | Pass | 5 | Pass | 5.2 | Pass | 5.4 | Pass | 6.2 |  | 5.3 | Pass | 8.54 | Pass | 6.17 | Pass | 6.12 | Pass | 6.4 | Pass
10 | 4.6 | 4.1 | 6.6 |  | 4.6 |  | 4.7 | Pass | 4.5 | Pass | 5.5 | Pass | 4.6 | Pass | 5.8 |  | 4.8 | Pass | 6.98 | Pass | 6.02 | Pass | 5.99 | Pass | 6.6 | Pass
11 | 5 | 4.2 | 4.5 |  | 4.6 |  | 4.9 | Pass | 4.7 | Pass | 5.5 | Pass | 5 | Pass | 5.8 |  | 4.4 | Pass | 8.32 | Pass | 5.98 | Pass | 5.57 | Pass | 6.4 | Pass
12 | 4.4 | 4.9 | 5.4 |  | 4.8 |  | 4.6 | Pass | 4.7 | Pass | 5.1 | Pass | 5.1 | Pass | 5.6 |  | 4.6 | Pass | 8.96 | Pass | 6.06 | Pass | 6.09 | Pass | 7.5 | Pass
13 | 4.3 | 4.1 | 5.6 |  | 4.7 |  | 4.3 | Pass | 4.4 | Pass | 5.1 | Pass | 5.1 | Pass | 5.3 |  | 4.7 | Pass | 7.07 | Pass | 5.79 | Pass | 5.85 | Pass | 6.8 | Pass
14 | 5 | 4.8 | 4.5 |  | 4.5 |  | 4 | Pass | 4.4 | Pass | 5.4 | Pass | 4.9 | Pass | 5.7 |  | 4.9 | Pass | 9.47 | Warning | 7.2 | Pass | 6.21 | Pass | 7 | Pass
15 | 4.7 | 4.9 | 5.1 |  | 4 |  | 4.1 | Pass | 4.3 | Pass | 5.5 | Pass | 4.7 | Pass | 5.6 |  | 4.7 | Pass | 8.06 | Pass | 5.94 | Pass | 5.47 | Pass | 7 | Pass
16 | 3.9 | 4.4 | 5.4 |  | 4.2 |  | 4.3 | Pass | 4.4 | Pass | 5.2 | Pass | 4.6 | Pass | 6 |  | 4.8 | Pass | 5.22 | Pass | 7.45 | Pass | 6.13 | Pass | 7 | Pass
17 | 4.1 | 3.9 | 5.6 |  | 4.3 |  | 3.9 | Pass | 4.5 | Pass | 5.5 | Pass | 4.7 | Pass | 5.4 |  | 4.9 | Pass | 7.23 | Pass | 7.11 | Pass | 6.37 | Pass | 5.6 | Pass
18 | 4.6 | 4.4 | 5.1 |  | 4.7 |  | 4.5 | Pass | 4.6 | Pass | 5.4 | Pass | 4.8 | Pass | 5.5 |  | 4.8 | Pass | 18.05 | Fail | 6.09 | Pass | 6 | Pass | 7 | Pass
19 | 5.7 | 4.7 | 6.2 |  | 4.8 |  | 4.1 | Pass | 5.5 | Pass | 5.1 | Pass | 5.1 | Pass | 5.9 |  | 4.8 | Pass | 7.3 | Pass | 6.09 | Pass | 6.06 | Pass | 6.2 | Pass
20 | 4 | 3.9 | 4.7 |  | 4.5 |  | 4.5 | Pass | 5.6 | Pass | 5.5 | Pass | 4.5 | Pass | 5.2 |  | 5 | Pass | 7.74 | Pass | 6.66 | Pass | 6.46 | Pass | 5.9 | Pass
21 | 4.3 | 4.5 | 4.7 |  | 4.8 |  | 5.3 | Pass | 5.4 | Pass | 5.4 | Pass | 4.7 | Pass | 10.6 | Warning | 5 | Pass | 7.67 | Pass | 5.75 | Pass | 5.67 | Pass | 6.5 | Pass
22 | 4.6 | 3.8 | 4.7 |  | 4.3 |  | 4.7 | Pass | 5 | Pass | 5.3 | Pass | 4.8 | Pass | 6.2 |  | 5 | Pass | 8.98 | Pass | 14.47 | Fail | 12.05 | Fail | 6.7 | Pass
23 | 4.3 | 4.9 | 5.3 |  | 4.4 |  | 4.5 | Pass | 4.9 | Pass | 5.2 | Pass | 5.3 | Pass | 5.4 |  | 4.7 | Pass | 7.46 | Pass | 5.65 | Pass | 5.53 | Pass | 8.6 | Pass
24 | 4.3 | 4.6 | 4.5 |  | 4.6 |  | 4.1 | Pass | 4.4 | Pass | 5.2 | Pass | 5.3 | Pass | 5.6 |  | 4.9 | Pass | 10.37 | Warning | 6.41 | Pass | 5.97 | Pass | 6.8 | Pass
25 | 4.2 | 4.3 | 4.7 |  | 4.3 |  | 4.2 | Pass | 4.3 | Pass | 5.3 | Pass | 4.7 | Pass | 6.2 |  | 4.6 | Pass | 8.59 | Pass | 5.96 | Pass | 5.83 | Pass | 6.8 | Pass
26 | 4.3 | 4.3 | 4.6 |  | 4.5 |  | 4.2 | Pass | 4.4 | Pass | 5.3 | Pass | 4.5 | Pass | 5.9 |  | 4.8 | Pass | 7.14 | Pass | 6.81 | Pass | 5.77 | Pass | 6.8 | Pass
27 | 4.2 | 4.1 | 4.2 |  | 4.4 |  | 4.2 | Pass | 4.4 | Pass | 5.1 | Pass | 4.7 | Pass | 5.8 |  | 4.7 | Pass | 8.63 | Pass | 6.19 | Pass | 5.8 | Pass | 7.1 | Pass
28 | 4.1 | 3.8 | 4.8 |  | 4.6 |  | 4.4 | Pass | 4.8 | Pass | 5 | Pass | 4.5 | Pass | 6.6 |  | 4.8 | Pass | 12.38 | Fail | 6.31 | Pass | 6.27 | Pass | 6 | Pass
29 | 4.4 | 4.1 | 5 |  | 4.5 |  | 5.7 | Pass | 4.8 | Pass | 5.1 | Pass | 4.8 | Pass | 7 |  | 4.6 | Pass | 8.33 | Pass | 5.66 | Pass | 5.23 | Pass | 5.5 | Pass
30 | 4.1 | 4.3 | 4.6 |  | 4.4 |  | 4.5 | Pass | 5.1 | Pass | 5.2 | Pass | 5.3 | Pass | 5.7 |  | 5 | Pass | 7.33 | Pass | 6.17 | Pass | 6.17 | Pass | 5.6 | Pass
31 | 4.2 | 3.9 | 5 |  | 4.5 |  | 4.2 | Pass | 5 | Pass | 5.3 | Pass | 4.8 | Pass | 5.6 |  | 4.5 | Pass | 7.11 | Pass | 5.65 | Pass | 5.52 | Pass | 6.3 | Pass
32 | 4.4 | 4.7 | 4.3 |  | 4.2 |  | 4.6 | Pass | 5 | Pass | 5.1 | Pass | 4.5 | Pass | 5.1 |  | 5.1 | Pass | 7.36 | Pass | 5.8 | Pass | 5.89 | Pass | 5.7 | Pass
33 | 4.4 | 4 | 4.6 |  | 5.1 |  | 4.6 | Pass | 5.2 | Pass | 4.9 | Pass | 5.1 | Pass | 6 |  | 4.4 | Pass | 9999 | Fail | 5.34 | Pass | 5.28 | Pass | 7.3 | Pass
34 | 4.2 | 4.6 | 5.3 |  | 5.2 |  | 4.1 | Pass | 4.4 | Pass | 5.2 | Pass | 4.8 | Pass | 5.8 |  | 4.8 | Pass | 7.73 | Pass | 6.87 | Pass | 6.29 | Pass | 7.2 | Pass
35 | 4.3 | 4.7 | 4.3 |  | 4.2 |  | 4.1 | Pass | 4.4 | Pass | 5.2 | Pass | 4.6 | Pass | 5.9 |  | 4.8 | Pass | 6.46 | Pass | 6.4 | Pass | 5.9 | Pass | 6.3 | Pass
36 | 4.2 | 4.2 | 4.7 |  | 4.1 |  | 4.1 | Pass | 4.4 | Pass | 5.1 | Pass | 4.7 | Pass | 5.5 |  | 4.8 | Pass | 7.04 | Pass | 6.48 | Pass | 6 | Pass | 6.5 | Pass
37 | 4.5 | 4.4 | 4.4 |  | 4.6 |  | 4.2 | Pass | 4.4 | Pass | 5.1 | Pass | 4.6 | Pass | 6.8 |  | 4.7 | Pass | 6.79 | Pass | 6.73 | Pass | 6.16 | Pass | 6.6 | Pass
38 | 4.4 | 4.5 | 4.8 |  | 4.6 |  | 4.1 | Pass | 4.1 | Pass | 5.1 | Pass | 4.6 | Pass | 6.2 |  | 4.6 | Pass | 6.38 | Pass | 7.92 | Pass | 7.92 | Pass | 6.2 | Pass
39 | 4.2 | 3.6 | 3.9 |  | 4.1 |  | 4.4 | Pass | 4.7 | Pass | 5.2 | Pass | 5.2 | Pass | 5.6 |  | 5.1 | Pass | 7.11 | Pass | 6.04 | Pass | 6.29 | Pass | 14.1 | Fail
40 | 4.8 | 4.6 | 3.7 |  | 5.6 |  | 4.1 | Pass | 5.1 | Pass | 5.1 | Pass | 5.1 | Pass | 5.4 |  | 4.6 | Pass | 10.23 | Warning | 5.59 | Pass | 5.52 | Pass | 6.1 | Pass
41 | 5 | 4.4 | 3.9 |  | 5.6 |  | 5.1 | Pass | 5.1 | Pass | 5 | Pass | 4.4 | Pass | 5.7 |  | 4.5 | Pass | 6.59 | Pass | 5.23 | Pass | 5.24 | Pass | 7.9 | Pass
42 | 4.2 | 4.6 | 3.8 |  | 4.6 |  | 4.7 | Pass | 5.2 | Pass | 5.6 | Pass | 5.2 | Pass | 4.9 |  | 5.4 | Pass | 7.62 | Pass | 7.81 | Pass | 8.07 | Pass | 8.3 | Pass
43 | 4.4 | 4.1 | 3.9 |  | 4.7 |  | 4.2 | Pass | 4.4 | Pass | 5.4 | Pass | 5.8 | Pass | 4.9 |  | 5 | Pass | 8.99 | Pass | 6.74 | Pass | 6 | Pass | 8.1 | Pass
44 | 4.3 | 4.1 | 3.4 |  | 5.1 |  | 4.1 | Pass | 4.6 | Pass | 5.6 | Pass | 4.8 | Pass | 5 |  | 5.2 | Pass | 6.27 | Pass | 7.39 | Pass | 7.07 | Pass | 7.6 | Pass
45 | 4.2 | 5.4 | 3.7 |  | 4.3 |  | 4 | Pass | 4.5 | Pass | 5.4 | Pass | 5.2 | Pass | 5.2 |  | 5.1 | Pass | 6.1 | Pass | 6.9 | Pass | 6.44 | Pass | 8.2 | Pass
46 | 4.7 | 4.4 | 3.4 |  | 4.4 |  | 4 | Pass | 4.4 | Pass | 5.3 | Pass | 5.4 | Pass | 5.1 |  | 4.9 | Pass | 5.68 | Pass | 7.42 | Pass | 6.49 | Pass | 7.1 | Pass
47 | 4.5 | 3.9 | 3.6 |  | 4.3 |  | 4.2 | Pass | 4.4 | Pass | 5.8 | Pass | 4.7 | Pass | 4.9 |  | 5.1 | Pass | 8.3 | Pass | 19.83 | Fail | 17.51 | Fail | 15.3 | Fail
48 | 4.4 | 5 | 3.5 |  | 5.4 |  | 4.1 | Pass | 4.5 | Pass | 5.4 | Pass | 4.9 | Pass | 5.2 |  | 5.2 | Pass | 6.76 | Pass | 7.15 | Pass | 7.15 | Pass | 6.9 | Pass
49 | 4.7 | 4.6 | 4.2 |  | 4.3 |  | 4.6 | Pass | 4.8 | Pass | 5.2 | Pass | 5.1 | Pass | 5.2 |  | 4.8 | Pass | 6.79 | Pass | 6.16 | Pass | 6.12 | Pass | 6.3 | Pass
50 | 4.5 | 4.4 | 4 |  | 3.8 |  | 4.9 | Pass | 5.5 | Pass | 6.3 | Pass | 4.7 | Pass | 5.7 |  | 5.8 | Pass | 6.38 | Pass | 11.44 | Warning | 11.45 | Warning | 8 | Pass
51 | 4.3 | 4.1 | 4 |  | 4.6 |  | 4.8 | Pass | 5.2 | Pass | 5.5 | Pass | 5.6 | Pass | 4.9 |  | 4.9 | Pass | 5.98 | Pass | 6.46 | Pass | 6.95 | Pass | 13.4 | Fail
52 | 4.4 | 3.9 | 3.4 |  | 5.2 |  | 4.7 | Pass | 5.7 | Pass | 5.2 | Pass | 5.7 | Pass | 5.2 |  | 4.8 | Pass | 6.65 | Pass | 5.96 | Pass | 5.9 | Pass | 7 | Pass
53 | 4.4 | 4.2 | 3.8 |  | 4.7 |  | 4.2 | Pass | 4.6 | Pass | 5.6 | Pass | 5.3 | Pass | 5.2 |  | 5.7 | Pass | 7.52 | Pass | 6.74 | Pass | 6.34 | Pass | 7.9 | Pass
54 | 4.6 | 4.4 | 3.8 |  | 4.1 |  | 4.2 | Pass | 4.5 | Pass | 5.6 | Pass | 4.9 | Pass | 5 |  | 5.2 | Pass | 6.71 | Pass | 14.57 | Fail | 13.92 | Fail | 18.7 | Fail
55 | 4.5 | 4.4 | 3.8 |  | 5.1 |  | 4.2 | Pass | 4.3 | Pass | 5.2 | Pass | 5 | Pass | 5.5 |  | 4.7 | Pass | 6.54 | Pass | 6.26 | Pass | 5.9 | Pass | 7.8 | Pass
56 | 4.6 | 3.9 | 3.9 |  | 3.9 |  | 4.2 | Pass | 4.3 | Pass | 5.2 | Pass | 4.6 | Pass | 4.9 |  | 4.7 | Pass | 5.34 | Pass | 6.76 | Pass | 6.35 | Pass | 7.8 | Pass
57 | 4.5 | 4.2 | 3.5 |  | 4.3 |  | 4.3 | Pass | 4.4 | Pass | 5.5 | Pass | 4.6 | Pass | 5 |  | 5.1 | Pass | 9.24 | Warning | 6.93 | Pass | 6.34 | Pass | 8.1 | Pass
58 | 4.5 | 5 | 3.5 |  | 4.4 |  | 4.3 | Pass | 4.4 | Pass | 5.4 | Pass | 4.9 | Pass | 4.7 |  | 5 | Pass | 7.4 | Pass | 7.9 | Pass | 6.67 | Pass | 6.5 | Pass
59 | 4.5 | 4.6 | 3.8 |  | 5 |  | 4.8 | Pass | 5 | Pass | 5.5 | Pass | 4.8 | Pass | 4.9 |  | 5.2 | Pass | 6.41 | Pass | 7.23 | Pass | 7.21 | Pass | 8.9 | Pass
60 | 4.8 | 4 | 3.4 |  | 4.7 |  | 4.7 | Pass | 4.9 | Pass | 5.7 | Pass | 4.8 | Pass | 5.4 |  | 5.2 | Pass | 6.12 | Pass | 6.58 | Pass | 6.57 | Pass | 5.5 | Pass
61 | 5.7 | 4.9 | 3.9 |  | 5 |  | 4.9 | Pass | 5 | Pass | 5.5 | Pass | 5.2 | Pass | 4.7 |  | 4.9 | Pass | 7.1 | Pass | 6.21 | Pass | 6.14 | Pass | 8.4 | Pass
62 | 4.6 | 4.4 | 3.8 |  | 4.7 |  | 4.9 | Pass | 5.2 | Pass | 5.2 | Pass | 5.5 | Pass | 5.1 |  | 4.8 | Pass | 7.23 | Pass | 6.4 | Pass | 6.34 | Pass | 9 | Pass
63 | 4.7 | 4 | 3.4 |  | 4.6 |  | 4.7 | Pass | 4.7 | Pass | 5.5 | Pass | 5.2 | Pass | 4.8 |  | 5 | Pass | 6.58 | Pass | 7.4 | Pass | 7.88 | Pass | 9.2 | Warning
64 | 4.3 | 3.9 | 4.1 |  | 4.2 |  | 4 | Pass | 4.4 | Pass | 5.7 | Pass | 4.6 | Pass | 5.2 |  | 5.5 | Pass | 6.25 | Pass | 10.45 | Warning | 9.97 | Warning | 7.3 | Pass
65 | 4.5 | 4.3 | 3.6 |  | 4.4 |  | 4.2 | Pass | 4.6 | Pass | 5.2 | Pass | 5.1 | Pass | 5.1 |  | 4.7 | Pass | 6.15 | Pass | 5.59 | Pass | 5.37 | Pass | 6.7 | Pass
66 | 4.6 | 4.4 | 3.9 |  | 4.8 |  | 4.4 | Pass | 4.7 | Pass | 5.7 | Pass | 5.1 | Pass | 4.8 |  | 5.2 | Pass | 5.85 | Pass | 6.83 | Pass | 6.63 | Pass | 6.5 | Pass
67 | 5 | 4.1 | 3.9 |  | 5.3 |  | 4.4 | Pass | 5.3 | Pass | 5.7 | Pass | 5.6 | Pass | 4.8 |  | 5.3 | Pass | 14.25 | Fail | 7.18 | Pass | 6.95 | Pass | 10.8 | Warning
68 | 4 | 3.9 | 3.7 |  | 4.1 |  | 4.9 | Pass | 5.1 | Pass | 5.5 | Pass | 5.5 | Pass | 5.5 |  | 5.1 | Pass | 6.38 | Pass | 7.81 | Pass | 7.84 | Pass | 8.2 | Pass
69 | 4.3 | 3.8 | 3.8 |  | 3.9 |  | 4.5 | Pass | 4.3 | Pass | 5.7 | Pass | 4.7 | Pass | 5 |  | 5 | Pass | 5.85 | Pass | 6.8 | Pass | 6.76 | Pass | 7 | Pass
70 | 4.5 | 4.5 | 3.8 |  | 4.5 |  | 4.9 | Pass | 4.4 | Pass | 5.3 | Pass | 4.8 | Pass | 4.7 |  | 4.9 | Pass | 6.21 | Pass | 6.16 | Pass | 6.18 | Pass | 7.3 | Pass
71 | 4.6 | 4.7 | 4 |  | 4.9 |  | 4.1 | Pass | 4.7 | Pass | 5.4 | Pass | 5.2 | Pass | 4.9 |  | 4.9 | Pass | 10.72 | Warning | 6.58 | Pass | 7.34 | Pass | 6.7 | Pass
72 | 4.4 | 4.1 | 4.2 |  | 4.4 |  | 4.7 | Pass | 5 | Pass | 5.1 | Pass | 5.7 | Pass | 5 |  | 5.4 | Pass | 6.07 | Pass | 6.87 | Pass | 6.95 | Pass | 7.4 | Pass
73 | 4.4 | 4 | 4 |  | 5 |  | 4.8 | Pass | 4.7 | Pass | 5.6 | Pass | 5.5 | Pass | 5.1 |  | 5.2 | Pass | 6.95 | Pass | 6.94 | Pass | 9 | Pass | 8.6 | Pass
74 | 5.1 | 4.5 | 4.1 |  | 4.6 |  | 4.4 | Pass | 4.5 | Pass | 5.9 | Pass | 4.7 | Pass | 4.8 |  | 5.7 | Pass | 18.44 | Fail | 9.01 | Warning | 6.2 | Pass | 7.7 | Pass
75 | 4 | 4.5 | 4 |  | 4.5 |  | 4.4 | Pass | 4.4 | Pass | 5.4 | Pass | 4.7 | Pass | 5.7 |  | 4.9 | Pass | 6.34 | Pass | 6.33 | Pass | 6.6 | Pass | 7.6 | Pass
76 | 4.9 | 4.6 | 3.8 |  | 5.2 |  | 4.2 | Pass | 4.4 | Pass | 5.3 | Pass | 4.8 | Pass | 4.7 |  | 4.9 | Pass | 6.34 | Pass | 6.99 | Pass | 7.1 | Pass | 6.3 | Pass
77 | 4.3 | 4.2 | 3.6 |  | 4.6 |  | 4.4 | Pass | 4.6 | Pass | 5.3 | Pass | 4.8 | Pass | 5.4 |  | 4.9 | Pass | 6.94 | Pass | 6.57 | Pass | 7.5 | Pass | 11.6 | Warning
78 | 4.5 | 4.3 | 3.3 |  | 4.4 |  | 5.2 | Pass | 5.5 | Pass | 5.4 | Pass | 5.8 | Pass | 5.3 |  | 5 | Pass | 6.08 | Pass | 8.75 | Pass | 8.3 | Pass | 8.4 | Pass
79 | 4.4 | 4.4 | 3.5 |  | 4.4 |  | 4.2 | Pass | 4.5 | Pass | 5.7 | Pass | 4.9 | Pass | 5.2 |  | 5.3 | Pass | 7.98 | Pass | 7.73 | Pass | 6 | Pass | 7.4 | Pass
80 | 4.6 | 4.6 | 4.1 |  | 4.4 |  | 4.1 | Pass | 4.9 | Pass | 5.5 | Pass | 6.3 | Pass | 5.1 |  | 5.1 | Pass | 5.79 | Pass | 6.75 | Pass | 10.6 | Warning | 6.8 | Pass
81 | 4.9 | 4.7 | 4 |  | 5 |  | 5.1 | Pass | 5.4 | Pass | 6.2 | Pass | 5.4 | Pass | 4.8 |  | 6.1 | Pass | 5.53 | Pass | 11.98 | Warning | 7.9 | Pass | 8.5 | Pass
82 | 4.7 | 4.8 | 3.9 |  | 5 |  | 4.6 | Pass | 4.4 | Pass | 6.1 | Pass | 4.9 | Pass | 4.7 |  | 5.7 | Pass | 6.24 | Pass | 7.41 | Pass | 5.7 | Pass | 12.6 | Fail
83 | 4.6 | 4.4 | 3.5 |  | 4.5 |  | 4.4 | Pass | 4.6 | Pass | 5.4 | Pass | 5 | Pass | 5 |  | 5.1 | Pass | 7.71 | Pass | 6.86 | Pass | 6.6 | Pass | 8.8 | Pass
84 | 4.5 | 4.1 | 3.6 |  | 4.4 |  | 4.4 | Pass | 4.8 | Pass | 5.5 | Pass | 5.5 | Pass | 4.9 |  | 5.3 | Pass | 5.99 | Pass | 7.17 | Pass | 6.2 | Pass | 11.6 | Warning
85 | 4.5 | 5 | 3.6 |  | 4.1 |  | 4.6 | Pass | 4.6 | Pass | 6 | Pass | 5 | Pass | 4.6 |  | 5.7 | Pass | 5.9 | Pass | 7.83 | Pass | 6.2 | Pass | 11 | Warning
86 | 4.3 | 4.5 | 3.8 |  | 4 |  | 4.5 | Pass | 5 | Pass | 5.6 | Pass | 5.8 | Pass | 4.6 |  | 5.2 | Pass | 5.8 | Pass | 9.03 | Warning | 7.8 | Pass | 8 | Pass
87 | 4.5 | 4.4 | 3.2 |  | 4.4 |  | 4.5 | Pass | 5 | Pass | 6.4 | Pass | 5.5 | Pass | 4.5 |  | 6 | Pass | 6.16 | Pass | 9999 | Fail | 12 | Warning | 11.1 | Warning
88 | 4.7 | 4.4 | 3.9 |  | 4.9 |  | 4.6 | Pass | 5.8 | Pass | 6 | Pass | 5.6 | Pass | 4.7 |  | 5.8 | Pass | 5.24 | Pass | 7.36 | Pass | 8.1 | Pass | 14.4 | Fail
89 | 4.6 | 4.5 | 3.9 |  | 4.6 |  | 4.6 | Pass | 5.6 | Pass | 6.4 | Pass | 5.4 | Pass | 4.7 |  | 5.8 | Pass | 5.72 | Pass | 6.74 | Pass | 10.9 | Warning | 10.5 | Warning
90 | 4.8 | 4.4 | 3.7 |  | 4.6 |  | 4.8 | Pass | 5.3 | Pass | 6.1 | Pass | 5.7 | Pass | 4.8 |  | 5.8 | Pass | 5.49 | Pass | 7.31 | Pass | 9.4 | Warning | 7.2 | Pass
91 | 5.3 | 4.3 | 3.8 |  | 4.7 |  | 5.6 | Pass | 5.2 | Pass | 6 | Pass | 5.7 | Pass | 4.8 |  | 5.4 | Pass | 5.95 | Pass | 8.87 | Pass | 7.2 | Pass | 6.8 | Pass
92 | 4.7 | 4.4 | 4 |  | 5.3 |  | 4.9 | Pass | 5.2 | Pass | 6.2 | Pass | 6.1 | Pass | 4.6 |  | 5.9 | Pass | 5.87 | Pass | 13.49 | Fail | 9.8 | Warning | 9.2 | Warning
93 | 4.5 | 4.5 | 4.5 |  | 4.9 |  | 4.5 | Pass | 4.8 | Pass | 6.6 | Pass | 5.5 | Pass | 4.7 |  | 6.6 | Pass | 6.58 | Pass | 10.02 | Warning | 13 | Fail | 176.3 | Fail
94 | 5.1 | 4.2 | 3.8 |  | 4.3 |  | 4.6 | Pass | 4.9 | Pass | 6.1 | Pass | 6.1 | Pass | 4.6 |  | 5.7 | Pass | 5.75 | Pass | 7.83 | Pass | 9 | Pass | 9 | Pass
95 | 4.2 | 4.1 | 3.7 |  | 4.4 |  | 4.2 | Pass | 5.2 | Pass | 6 | Pass | 6 | Pass | 4.9 |  | 5.7 | Pass | 5.82 | Pass | 9.36 | Warning | 7.3 | Pass | 7.8 | Pass
96 | 4.7 | 4.1 | 3.8 |  | 4.9 |  | 4.4 | Pass | 4.7 | Pass | 6.7 | Pass | 5.2 | Pass | 5.1 |  | 6.2 | Pass | 5.75 | Pass | 11.09 | Warning | 7.7 | Pass | 8.1 | Pass
97 | 4.8 | 4.4 | 4 |  | 4.6 |  | 4.3 | Pass | 4.9 | Pass | 5.8 | Pass | 5.5 | Pass | 5.1 |  | 5.5 | Pass | 5.82 | Pass | 7.85 | Pass | 7.4 | Pass | 7.7 | Pass
98 | 4.5 | 3.9 | 4 |  | 4.1 |  | 4.2 | Pass | 5.4 | Pass | 5.9 | Pass | 5.8 | Pass | 5.1 |  | 5.8 | Pass | 5.54 | Pass | 9.48 | Warning | 142.6 | Fail | 7.5 | Pass
99 | 4.5 | 4.6 | 3.8 |  | 4.6 |  | 4.5 | Pass | 5.2 | Pass | 6.3 | Pass | 5.6 | Pass | 4.8 |  | 6.3 | Pass | 15.21 | Fail | 7.71 | Pass | 8 | Pass | 8.7 | Pass
100 | 4.5 | 4.1 | 3.8 |  | 4.3 |  | 4.6 | Pass | 4.6 | Pass | 6.5 | Pass | 5.2 | Pass | 4.6 |  | 6 | Pass | 5.62 | Pass | 8.15 | Pass | 6.7 | Pass | 21 | Fail
101 | 10 | 11.2 |  | Battery reading did not come | 10.6 | Replaced on 2/2/2018 | 4.6 | Pass | 4.8 | Pass | 6.1 | Pass | 5.4 | Pass | 4.9 |  | 5.4 | Pass | 6.68 | Pass | 8.28 | Pass | 7.3 | Pass | 10.1 | Warning
102 | 4.3 | 4.3 | 4 |  | 4.5 |  | 4.5 | Pass | 4.8 | Pass | 6 | Pass | 5.6 | Pass | 4.9 |  | 5.7 | Pass | 5.92 | Pass | 19.89 | Fail | 7.1 | Pass | 7.7 | Pass
103 | 4.3 | 4 | 3.7 |  | 4.4 |  | 4.3 | Pass | 4.6 | Pass | 6.2 | Pass | 5 | Pass | 5.1 |  | 6.1 | Pass | 5.94 | Pass | 7.41 | Pass | 6.7 | Pass | 11.3 | Warning
104 | 4.1 | 3.9 | 4 |  | 4.3 |  | 4.3 | Pass | 5.1 | Pass | 5.5 | Pass | 10.3 | Pass | 4.7 |  | 5.3 | Pass | 6.2 | Pass | 5.49 | Pass | 8.4 | Pass | 7.3 | Pass
105 | 4.2 | 4.1 | 3.5 |  | 4.4 |  | 4.5 | Pass | 4.8 | Pass | 7.9 | Pass | 5.7 | Pass | 4.5 |  | 11.4 | Warning | 6.03 | Pass | 8.88 | Pass | 7.4 | Pass | 8.5 | Pass
106 | 4.4 | 4.4 | 3.8 |  | 4.6 |  | 4.5 | Pass | 4.7 | Pass | 6.2 | Pass | 5.4 | Pass | 4.3 |  | 5.9 | Pass | 5.47 | Pass | 10.57 | Waring | 10.8 | Warning | 11.3 | Warning
107 | 4.4 | 4.4 | 3.8 |  | 4.6 |  | 4.7 | Pass | 4.7 | Pass | 5.9 | Pass | 5.2 | Pass | 4.7 |  | 5.7 | Pass | 6.07 | Pass | 8.51 | Pass | 7.7 | Pass | 12 | Warning
108 | 4.3 | 4.5 | 3.7 |  | 4.4 |  | 4.3 | Pass | 4.8 | Pass | 5.7 | Pass | 5.4 | Pass | 4.6 |  | 5.3 | Pass | 5.66 | Pass | 10.05 | Warning | 9.7 | Warning | 8.1 | Pass
109 | 4.4 | 4.4 | 3.6 |  | 4.7 |  | 4.8 | Pass | 5.1 | Pass | 6 | Pass | 5.8 | Pass | 4.8 |  | 5.8 | Pass | 5.93 | Pass | 8.59 | Pass | 10.8 | Warning | 9.7 | Warning
110 | 4.3 | 4.5 | 4.1 |  | 4.5 |  | 4.3 | Pass | 4.5 | Pass | 6.3 | Pass | 5 | Pass | 4.7 |  | 6.1 | Pass | 5.47 | Pass | 7.42 | Pass | 6.9 | Pass | 7.6 | Pass
111 | 4.7 | 4.7 | 3.9 |  | 4.8 |  | 4.6 | Pass | 5 | Pass | 5.6 | Pass | 5.7 | Pass | 4.8 |  | 5.3 | Pass | 6.61 | Pass | 8.88 | Pass | 8.8 | Pass | 8.1 | Pass
112 | 4.4 | 4.5 | 3.7 |  | 4.6 |  | 4.5 | Pass | 4.7 | Pass | 6.2 | Pass | 5.2 | Pass | 4.5 |  | 6.1 | Pass | 6.56 | Pass | 8.02 | Pass | 6.9 | Pass | 11.8 | Warning
113 | 4.3 | 4.2 | 4.1 |  | 4.4 |  | 4.3 | Pass | 5.3 | Pass | 5.7 | Pass | 5.9 | Pass | 5.3 |  | 5.3 | Pass | 6.28 | Pass | 11.97 | Warning | 8.2 | Pass | 8 | Pass
114 | 4.2 | 4.7 | 3.7 |  | 4.6 |  | 4.4 | Pass | 4.9 | Pass | 6.5 | Pass | 5.6 | Pass | 4.9 |  | 6.3 | Pass | 5.8 | Pass | 10.43 | Warning | 10.4 | Warning | 11.3 | Warning
115 | 4.2 | 4 | 4.1 |  | 4.5 |  | 4.4 | Pass | 4.8 | Pass | 6.1 | Pass | 5.4 | Pass | 4.4 |  | 5.9 | Pass | 5.82 | Pass | 8.25 | Pass | 7 | Pass | 10.1 | Warning
116 | 4.3 | 4.8 | 3.6 |  | 4.8 |  | 4.6 | Pass | 4.7 | Pass | 5.9 | Pass | 5.1 | Pass | 4.4 |  | 5.6 | Pass | 6.24 | Pass | 7.43 | Pass | 4.4 | Pass | 5.9 | Pass
117 | 4.2 | 3.9 | 4.1 |  | 5.5 |  | 4.2 | Pass | 4.8 | Pass | 5.6 | Pass | 5.8 | Pass | 5 |  | 5.4 | Pass | 4.92 | Pass | 11.12 | Warning | 7.2 | Pass | 8.5 | Pass
118 | 4.2 | 4.1 | 3.9 |  | 4.6 |  | 4.4 | Pass | 4.8 | Pass | 6 | Pass | 6 | Pass | 4.8 |  | 7.3 | Pass | 6.14 | Pass | 7.81 | Pass | 20.1 | Fail | 21.4 | Fail
119 | 4.3 | 4.5 | 3.6 |  | 4.4 |  | 4.4 | Pass | 4.1 | Pass | 6.1 | Pass | 5.5 | Pass | 4.2 |  | 5.7 | Pass | 5.82 | Pass | 9.48 | Warning | 7.3 | Pass | 8 | Fail
120 | 4.6 | 4.7 | 4.7 |  | 7.1 |  | 4.3 | Pass |  | Not Determined | 5.5 | Pass |  | Not Determined | 5.2 |  | 6 | Pass | 5.43 | Pass | 8.32 | Pass | 7.1 | Pass | 8.7 | Fail
[19 empty] | 106 | Pass | 99 | Pass | 103 | Pass
[19 empty] | 8 | Warning | 15 | Warning | 11 | Warning
[19 empty] | 6 | Fail | 6 | Fail | 6 | Fail
[19 empty] | 14 | Non-Healthy Batteries | 21 | Non-Healthy Batteries | 17 | Non-Healthy Batteries

## NMPF
Battery Spec: 12 Volts 120 AH
Brand: Exide Power Safe
Sr. No. | 2019-04-10 | Comments - 4/10/2019 | 20/1/2021 | Comments - 20/1/2021
1 | 3.4 | Pass | 3.41 | Pass
2 | 3.5 | Pass | 3.35 | Pass
3 | 3.7 | Pass | 3.61 | Pass
4 | 3.5 | Pass | 3.18 | Pass
5 | 3.4 | Pass | 3.46 | Pass
6 | 3.5 | Pass | 3.26 | Pass
7 | 3.4 | Pass | 3.34 | Pass
8 | 3.4 | Pass | 3.45 | Pass
9 | 3.3 | Pass | 3.22 | Pass
10 | 3.5 | Pass | 3.57 | Pass
11 | 3.4 | Pass | 3.4 | Pass
12 | 3.4 | Pass | 3.31 | Pass
13 | 3.3 | Pass | 3.57 | Pass
14 | 3.4 | Pass | 3.46 | Pass
15 | 3.3 | Pass | 3.45 | Pass
16 | 3.4 | Pass | 3.52 | Pass
17 | 3.4 | Pass | 3.65 | Pass
18 | 3.4 | Pass | 3.6 | Pass
19 | 3.5 | Pass | 3.63 | Pass
20 | 3.5 | Pass | 3.49 | Pass
21 | 3.4 | Pass | 3.3 | Pass
22 | 3.4 | Pass | 3.37 | Pass
23 | 3.5 | Pass | 3.4 | Pass
24 | 3.4 | Pass | 3.25 | Pass
25 | 3.4 | Pass | 3.59 | Pass
26 | 3.3 | Pass | 3.53 | Pass
27 | 3.2 | Pass | 3.59 | Pass
28 | 3.3 | Pass | 3.51 | Pass
29 | 3.3 | Pass | 3.48 | Pass
30 | 3.6 | Pass | 3.54 | Pass
31 | 3.3 | Pass | 3.43 | Pass
32 | 3.5 | Pass | 3.66 | Pass
33 | 3.4 | Pass | 3.57 | Pass
34 | 3.5 | Pass | 3.46 | Pass
35 | 3.5 | Pass | 3.51 | Pass
36 | 3.4 | Pass | 3.58 | Pass
37 | 3.4 | Pass | 3.39 | Pass
38 | 3.5 | Pass | 3.44 | Pass
39 | 3.5 | Pass | 3.55 | Pass
40 | 3.5 | Pass | 3.59 | Pass
41 | 3.4 | Pass | 3.38 | Pass
42 | 3.6 | Pass | 3.5 | Pass
43 | 3.5 | Pass | 3.4 | Pass
44 | 3.5 | Pass | 3.45 | Pass

## MBE Cells UPS
AL & PC CELL MBE LAB 10 KVA UPS
Battery Spec: | 12 Volts 100 AH
Brand: | Exide Power-Safe Plus
Sr. No. | 2019-01-03 | Comments - 1/3/2019 | 29/3/2019 | Comments - 29/3/2019 | 27/6/2019 | Comments - 27/6/2019 | 19/8/2019 | Comments - 19/8/2019 | 27/9/2019 | Comments - 27/9/2019 | 31/10/2019 | Comments - 31/10/2019 | 27/11/2019 | Comments - 27/11/2019 | 2020-03-02 | Comments - 3/2/2020 | 2020-07-12 | Comments - 7/12/2020 | 28/1/2021 | Comments - 28/1/2021 | 2021-03-09 | Comments - 3/9/2021
1 | 4 | Pass | 4 | Pass | 4.7 | Pass | 5.3 | Pass | 4.1 | Pass | 4.9 | Pass | 4.1 | Pass | 4.53 | Pass | 4.18 | Pass | 4.42 | Pass | 4.83 | Pass
2 | 4 | Pass | 3.9 | Pass | 5.1 | Pass | 4.8 | Pass | 4.1 | Pass | 5.6 | Pass | 4.4 | Pass | 4.51 | Pass | 5.15 | Pass | 5.29 | Pass | 5.3 | Pass
3 | 3.8 | Pass | 4.5 | Pass | 4.6 | Pass | 4.2 | Pass | 4.1 | Pass | 5 | Pass | 4.8 | Pass | 4.43 | Pass | 5.28 | Pass | 4.59 | Pass | 5.2 | Pass
4 | 4.4 | Pass | 3.9 | Pass | 4.7 | Pass | 4.1 | Pass | 4.1 | Pass | 4.9 | Pass | 4.1 | Pass | 5.19 | Pass | 5.41 | Pass | 4.97 | Pass | 5.19 | Pass
5 | 4.1 | Pass | 4 | Pass | 4.9 | Pass | 4.3 | Pass | 4.2 | Pass | 5 | Pass | 4.1 | Pass | 4.38 | Pass | 16.02 | Fail | 9999 | Fail | 9999 | Fail
6 | 4.2 | Pass | 5 | Pass | 5 | Pass | 4 | Pass | 4.1 | Pass | 4.3 | Pass | 4 | Pass | 4.78 | Pass | 4.12 | Pass | 4.13 | Pass | 5.1 | Pass
7 | 4.9 | Pass | 4 | Pass | 4.6 | Pass | 4.1 | Pass | 4.3 | Pass | 4.3 | Pass | 4.3 | Pass | 4.68 | Pass | 4.34 | Pass | 4.37 | Pass | 5.54 | Pass
8 | 4 | Pass | 4.1 | Pass | 4.7 | Pass | 4 | Pass | 4.1 | Pass | 4 | Pass | 4.1 | Pass | 4.1 | Pass | 4.16 | Pass | 4.2 | Pass | 4.1 | Pass
9 | 3.9 | Pass | 4.3 | Pass | 4.5 | Pass | 4.3 | Pass | 4 | Pass | 4.6 | Pass | 4 | Pass | 4.48 | Pass | 5.01 | Pass | 4.98 | Pass | 4.83 | Pass
10 | 4.1 | Pass | 4.1 | Pass | 4.3 | Pass | 4 | Pass | 4 | Pass | 4 | Pass | 4 | Pass | 4.26 | Pass | 4.23 | Pass | 4.2 | Pass | 4.05 | Pass
11 | 4.2 | Pass | 4.1 | Pass | 4.1 | Pass | 4 | Pass | 4 | Pass | 4 | Pass | 4 | Pass | 4.8 | Pass | 4.17 | Pass | 4.19 | Pass | 4.1 | Pass
12 | 4.2 | Pass | 5.1 | Pass | 5.9 | Pass | 4 | Pass | 4 | Pass | 5.1 | Pass | 4 | Pass | 3.99 | Pass | 7.04 | Pass | 8.92 | Pass | 8.54 | Pass
13 | 4 | Pass | 4.2 | Pass | 4.4 | Pass | 4.1 | Pass | 4.1 | Pass | 4.1 | Pass | 4.1 | Pass | 4.39 | Pass | 4.32 | Pass | 4.37 | Pass | 4.26 | Pass
14 | 4.4 | Pass | 4 | Pass | 4.5 | Pass | 5 | Pass | 5.1 | Pass | 3.9 | Pass | 5 | Pass | 6.27 | Pass | 4.15 | Pass | 4.14 | Pass | 4.1 | Pass
15 | 4.1 | Pass | 4.5 | Pass | 4.8 | Pass | 3.9 | Pass | 4 | Pass | 4 | Pass | 4 | Pass | 4.03 | Pass | 4.72 | Pass | 4.16 | Pass | 4.86 | Pass
16 | 4.3 | Pass | 4.9 | Pass | 4.4 | Pass | 4.2 | Pass | 4.1 | Pass | 4.3 | Pass | 4 | Pass | 4.03 | Pass | 4.4 | Pass | 4.6 | Pass | 5.28 | Pass
17 | 4.2 | Pass | 4 | Pass | 4.8 | Pass | 4 | Pass | 4.5 | Pass | 4 | Pass | 4.5 | Pass | 4.91 | Pass | 4.3 | Pass | 5.39 | Pass | 4.66 | Pass
18 | 4.3 | Pass | 3.8 | Pass | 5.5 | Pass | 3.8 | Pass | 3.9 | Pass | 3.8 | Pass | 3.9 | Pass | 3.95 | Pass | 4.13 | Pass | 4.96 | Pass | 4.06 | Pass
19 | 4.2 | Pass | 4.3 | Pass | 4.7 | Pass | 4.5 | Pass | 4.1 | Pass | 4.5 | Pass | 4.1 | Pass | 4.02 | Pass | 4.74 | Pass | 4.98 | Pass | 5.01 | Pass
20 | 4.2 | Pass | 3.9 | Pass | 4.6 | Pass | 3.9 | Pass | 4.1 | Pass | 3.9 | Pass | 4.1 | Pass | 4.06 | Pass | 4.25 | Pass | 4.15 | Pass | 7.7 | Pass
GAL 6 SC SIR MBE LAB 10 KVA UPS
Battery Spec: | 12 Volts 65 AH
Brand: | Exide Power-Safe Plus
Sr. No. | 2019-01-03 | Comments - 1/3/2019 | 29/3/2019 | Comments - 29/3/2019 | 27/6/2019 | Comments - 27/6/2019 | 19/8/2019 | Comments - 19/8/2019 | 27/9/2019 | Comments - 27/9/2019 | 31/10/2019 | Comments - 31/10/2019 | 27/11/2019 | Comments - 27/11/2019 |  |  |  | 2020-07-12 | Comments - 7/12/2020 |  | 27/4/2021 | Comments - 27/4/2021
1 | 9.4 | Pass | 9.5 | Pass | 11.4 | Pass | 11.6 | Pass | 28.8 | FAIL | 7.5 | Pass | 8.1 | Fail |  | 4.53 |  | 6.97 | Pass |  | 2.8 | Pass
2 | 8.8 | Pass | 8.2 | Pass | 8.6 | Pass | 8.5 | Pass | 290.3 | FAIL | 246.8 | Fail | 7.2 | Fail |  | 4.51 |  | 4.69 | Pass |  | 3.2 | Pass
3 | 9.5 | Pass | 8.3 | Pass | 9.1 | Pass | 9.7 | Pass | 9999 | FAIL | 6.6 | Pass | 11 | Fail |  | 4.43 |  | 6.61 | Pass |  | 3.2 | Pass
4 | 8.3 | Pass | 7.9 | Pass | 8.3 | Pass | 8.6 | Pass | 9999 | FAIL | 6.2 | Pass | 7.9 | Fail |  | 5.19 |  | 7.85 | Pass |  | 3.2 | Pass
5 | 9.1 | Pass | 8.7 | Pass | 9.7 | Pass | 10.9 | Pass | 9999 | FAIL | 6.7 | Pass | 6.2 | Fail |  | 4.38 |  | 7.18 | Pass |  | 3.4 | Pass
6 | 8.2 | Pass | 8.2 | Pass | 8.9 | Pass | 9.3 | Pass | 9999 | FAIL | 10 | Pass | 5.9 | Fail |  | 4.78 |  | 12.09 | Warning |  | 2.8 | Pass
7 | 7.6 | Pass | 8.5 | Pass | 9 | Pass | 9.4 | Pass | 9999 | FAIL | 5.7 | Pass | 9999 | Fail |  | 4.68 |  | 6.4 | Pass |  | 3.1 | Pass
8 | 7.9 | Pass | 9 | Pass | 9.6 | Pass | 10.2 | Pass | 9999 | FAIL | 8.9 | Pass | 5.2 | Pass |  | 4.1 |  | 10.37 | Pass |  | 3.5 | Pass
9 | 8.6 | Pass | 10.4 | Pass | 11.5 | Pass | 11 | Pass | 9999 | FAIL | 11.2 | Pass | 10.2 | Pass |  | 4.48 |  | 8.16 | Pass |  | 3.2 | Pass
10 | 8.1 | Pass | 8.2 | Pass | 8.8 | Pass | 9.2 | Pass | 9999 | FAIL | 8.7 | Pass | 5.5 | Pass |  | 4.26 |  | 7.21 | Pass |  | 3.2 | Pass
11 | 8.5 | Pass | 7.7 | Pass | 8 | Pass | 8.5 | Pass | 9999 | FAIL | 29.4 | Fail | 5.7 | Pass |  | 4.8 |  | 23.05 | Fail |  | 3 | Pass
12 | 9 | Pass | 7.9 | Pass | 8.3 | Pass | 8.8 | Pass | 9999 | FAIL | 10.2 | Pass | 5.7 | Pass |  | 3.99 |  | 9.75 | Pass |  | 3.2 | Pass
| 9.3 |  | 10 |  | 153.4 |  | 191.7 |  |  |  | 7.9 |  | 5.9 |  |  | 4.39 |  | 15.44 | Warning |  | 2.8 | Pass
GAL EURO MBE LAB LAHA SIR 10 KVA UPS | 7.7 | UPS Not In Use Since Sept 2018 | 9 |  | 10.7 |  | 10.4 |  |  |  | 136.6 |  | 26.7 |  |  | 6.27 |  | 9.95 | Pass |  | 2.6 | Pass
Battery Spec: 12 Volts 65 AH | 8.2 |  | 9.7 |  | 11.9 |  | 12.5 |  |  |  | 7.4 |  | 6.6 |  |  | 4.03 |  | 8 | Pass |  | 2.6 | Pass
Brand: Amara Raja QUANTA | 7.9 |  | 8.4 |  | 9.4 |  | 10.1 |  |  |  | 14.4 |  | 5.6 |  |  | 4.03 |  | 6.57 | Pass |  | 3.1 | Pass
Sr. No. | 2019-01-03 | Comments - 1/3/2019 | 29/3/2019 | Comments - 29/3/2019 | 27/6/2019 | Comments - 27/6/2019 | 19/8/2019 | Comments - 19/8/2019 | 27/9/2019 | Comments - 27/9/2019 | 31/10/2019 | Comments - 31/10/2019 | 27/11/2019 | Comments - 27/11/2019 |  | 4.91 |  | 25/1/2021 | Comments - 25/1/2021 |  | 2021-03-09 | Comments - 9/3/2021
1 | 4.2 |  | 7.2 |  | 7.6 |  | 9 |  | 4 |  | 6.4 |  | 4 |  | 4.07 | 3.95 |  | 9999 | Fail |  | 7.63 | Pass
2 | 6.8 |  | 7.1 |  | 7.2 |  | 12.4 |  | 4.2 |  | 7.4 |  | 4.9 |  | 4.92 | 4.02 |  | 4.61 | Pass |  | 7.9 | Pass
3 | 4.8 |  | 6.9 |  | 7.8 |  | 5.7 |  | 4.9 |  | 7.9 |  | 4.1 |  | 4.13 | 4.06 |  | 4.21 | Pass |  | 7.23 | Pass
4 | 4.2 |  | 4.4 |  | 7.6 |  | 6.6 |  | 7.2 |  | 7.7 |  | 4.1 |  | 6.39 |  |  | 4.29 | Pass |  | 8.67 | Pass
5 | 4.2 |  | 4.5 |  | 6.9 |  | 8.6 |  | 4.7 |  | 6.1 |  | 4.1 |  | 4.33 |  |  | 4.31 | Pass |  | 5.73 | Pass
6 | 6.8 |  | 4.4 |  | 9 |  | 12.3 |  | 4.2 |  | 10 |  | 4.1 |  | 4.76 |  |  | 4.1 | Pass |  | 13.46 | Warning
7 | 4.2 |  | 4.4 |  | 6 |  | 6.9 |  | 4.2 |  | 5.7 |  | 4.1 |  | 4.53 |  |  | 4.9 | Pass |  | 4.68 | Pass
8 | 4.3 |  | 4.6 |  | 8.9 |  | 7.1 |  | 9.2 |  | 9.9 |  | 4.7 |  | 4.9 |  |  | 4.09 | Pass |  | 10.82 | Pass
9 | 5.2 |  | 4.1 |  | 4.5 |  | 9.2 |  | 4.2 |  | 6.5 |  | 4 |  | 4.14 |  |  | 4.53 | Pass |  | 7.21 | Pass
10 | 4.6 |  | 4.2 |  | 4.4 |  | 7.6 |  | 4.4 |  | 6.4 |  | 4.2 |  | 4.36 |  |  | 4.01 | Pass |  | 7.41 | Pass
11 | 4.9 |  | 4.4 |  | 5 |  | 26.2 |  | 4.2 |  | 23.5 |  | 4.5 |  | 4.64 |  |  | 4.09 | Pass |  | 23.16 | Fail
12 | 4.8 |  | 4.2 |  | 7.3 |  | 11.3 |  | 4 |  | 8.1 |  | 4.1 |  | 4.21 |  |  | 4.03 | Pass |  | 9.95 | Pass
13 | 4.8 |  | 4.1 |  | 4 |  | 7.3 |  | 4.1 |  | 10.8 |  | 4 |  | 6.29 |  |  | 4.27 | Pass |  | 15.72 | Warning
14 | 4.8 |  | 4.1 |  | 6.3 |  | 161.5 |  | 4.2 |  | 6.2 |  | 4.8 |  | 7.55 |  |  | 8.9 | Pass |  | 10.54 | Pass
15 | 5.4 |  | 4.2 |  | 5.6 |  | 5.7 |  | 4.2 |  | 4.7 |  | 4.2 |  | 9 |  |  | 4.32 | Pass |  | 7.16 | Pass
16 | 4.7 |  | 4 |  | 6.4 |  | 12.1 |  | 3.9 |  | 4 |  | 4.6 |  | 11.4 |  |  | 4.49 | Pass |  | 6.96 | Pass
[21 empty] | 6.96 | Pass
New MBE 10 KVA
2021-03-09 | Comments - 9/3/2021 |  | 27/4/2021 | Comments - 27/4/2021
3.32 | Pass |  | 4.9 | Pass
3.16 | Pass |  | 4.8 | Pass
3.2 | Pass |  | 5.2 | Pass
3.18 | Pass |  | 4.1 | Pass
3.55 | Pass |  | 5.6 | Pass
3.14 | Pass |  | 4.6 | Pass
3.35 | Pass |  | 5.1 | Pass
3.49 | Pass |  | 4 | Pass
3.37 | Pass |  | 4.4 | Pass
3.24 | Pass |  | 4.6 | Pass
3.15 | Pass |  | 3.9 | Pass
2.75 | Pass |  | 4.2 | Pass
3.13 | Pass |  | 4.2 | Pass
2.93 | Pass |  | 4.2 | Pass
2.96 | Pass |  | 4.3 | Pass
2.91 | Pass |  | 4.4 | Pass

## Other IITBNF UPS
EC Lab 10 KVA UPS
Battery Spec: | 12 Volts 65 AH
Brand: | Exide Power-Safe
Sr. No. | 2019-01-03 | Comments - 1/3/2019 | 29/3/2019 | Comments - 29/3/2019 | 27/6/2019 | Comments - 27/6/2019 |  | 19/8/2019 | Comments - 19/8/2019 | 27/9/2019 | Comments - 27/9/2019 | 31/10/2019 | Comments - 31/10/2019 | 2019-02-12 | Comments - 2/12/2019 | 2020-09-01 | Comments - 9/1/2020 | 2020-08-12 | Comments - 8/12/2020 | 28/1/2021 | Comments - 28/1/2021 | 2021-09-03 | Comments - 9/3/2021 | 27/4/2021 | Comments - 27/4/2021
1 | 6.3 | Pass | 4.7 | Pass | 5.8 | Pass |  | 9.3 | Pass | 5.8 | Pass | 7.6 | Pass | 6.3 | Pass | 5.22 | Pass | 7.88 | Pass | 7.59 | Pass | 8.55 | Pass | 6.1 | Pass
2 | 6.4 | Pass | 4.9 | Pass | 6.1 | Pass |  | 9.8 | Pass | 7.1 | Pass | 7.5 | Pass | 8.3 | Pass | 5.45 | Pass | 8.85 | Pass | 6.67 | Pass | 12.04 | Warning | 7.1 | Pass
3 | 6.5 | Pass | 5.4 | Pass | 5 | Pass |  | 20.8 | Fail | 5.7 | Pass | 6.9 | Pass | 5.6 | Pass | 5.86 | Pass | 6.7 | Pass | 7.45 | Pass | 13.87 | Warning | 6.9 | Pass
4 | 7.5 | Pass | 6.2 | Pass | 5 | Pass |  | 9.2 | Pass | 4.9 | Pass | 5.2 | Pass | 5.5 | Pass | 5.61 | Pass | 6.31 | Pass | 6.46 | Pass | 9.66 | Pass | 9.1 | Pass
5 | 8 | Pass | 5.7 | Pass | 4.7 | Pass |  | 11.9 | Pass | 4.6 | Pass | 6.2 | Pass | 4.9 | Pass | 6.2 | Pass | 5.9 | Pass | 5.92 | Pass | 10.88 | Pass | 8.4 | Pass
6 | 5.2 | Pass | 5.2 | Pass | 5.7 | Pass |  | 11.1 | Pass | 5.5 | Pass | 5.6 | Pass | 5.6 | Pass | 5.84 | Pass | 6.39 | Pass | 6.52 | Pass | 10.33 | Pass | 6.9 | Pass
7 | 6.1 | Pass | 5.2 | Pass | 116.9 | Fail |  | 13 | Pass | 179.7 | Fail | 9999 | Fail | 9999 | Fail | 6.89 | Pass | 9999 | Fail | 9999 | Fail | 9.71 | Pass | 7.8 | Pass
8 | 6.1 | Pass | 6.5 | Pass | 7.1 | Pass |  | 9.4 | Pass | 6.9 | Pass | 6.7 | Pass | 9999 | Fail | 5.39 | Pass | 8 | Pass | 6.06 | Pass | 10.5 | Pass | 6.5 | Pass
9 | 5.5 | Pass | 6.5 | Pass | 5.7 | Pass |  | 10.5 | Pass | 6.6 | Pass | 7.7 | Pass | 4.9 | Pass | 9999 | Fail | 7.2 | Pass | 7.2 | Pass | 8.93 | Pass | 9999 | Fail
10 | 5 | Pass | 5.2 | Pass | 5.3 | Pass |  | 10.8 | Pass | 5.1 | Pass | 6 | Pass | 5.7 | Pass | 5.99 | Pass | 6.25 | Pass | 6.28 | Pass | 9.46 | Pass | 6 | Pass
11 | 5.2 | Pass | 6.8 | Pass | 6.1 | Pass |  | 12.7 | Warning | 6.2 | Pass | 6.2 | Pass | 5.2 | Pass | 5.86 | Pass | 6.82 | Pass | 9.83 | Pass | 12.18 | Warning | 7.5 | Pass
12 | 6.5 | Pass | 5.4 | Pass | 5.6 | Pass |  | 11.1 | Pass | 5.5 | Pass | 5.6 | Pass | 8.1 | Pass | 7.33 | Pass | 8.24 | Pass | 6.98 | Pass | 11.51 | Pass | 8.5 | Pass
13 | 6 | Pass | 5.8 | Pass | 6.2 | Pass |  | 15.6 | Warning | 6.4 | Pass | 6.5 | Pass | 5.8 | Pass | 6.69 | Pass | 8 | Pass | 7.41 | Pass | 9.55 | Pass | 8.7 | Pass
14 | 5.4 | Pass | 6.5 | Pass | 6.4 | Pass |  | 10.9 | Pass | 6.8 | Pass | 6.8 | Pass | 6.4 | Pass | 6.16 | Pass | 6.76 | Pass | 8.58 | Pass | 11.61 | Pass | 7.6 | Pass
15 | 6.5 | Pass | 5.4 | Pass | 5.5 | Pass |  | 11.2 | Pass | 5.4 | Pass | 5.5 | Pass | 6.9 | Pass | 6.52 | Pass | 9.14 | Pass | 7.06 | Pass | 8.58 | Pass | 9.1 | Pass
[8 empty] | 9.7 | [5 empty] | 5.5 | Pass
MCL UPS 1 15 KVA | [7 empty] | 8.8
Battery Spec: | 12 Volts 26 AH | [6 empty] | 9.3
Brand: | Exide Power-Safe | [6 empty] | 9.4
Sr. No. | 2019-01-03 | Comments - 1/3/2019 | 29/3/2019 | Comments - 29/3/2019 | 27/6/2019 | Comments - 27/6/2019 | 19/8/2019 | 9.5 | Comments - 19/8/2019 | 27/9/2019 | Comments - 27/9/2019 | 31/10/2019 | Comments - 31/10/2019 | 29/11/2019 | Comments - 29/11/2019 | 2020-09-01 | Comments - 9/1/2020 | 2020-08-12 | Comments - 8/12/2020 | 28/1/2021 | Comments - 28/1/2021 | 2021-09-03 | Comments - 9/3/2021 | 27/4/2021 | Comments - 27/4/2021
1 |  |  |  |  | 12.1 | Pass | 10 |  | Pass | 10.3 | Pass | 12.2 | Pass | 10.5 | Pass | 11.02 | Pass | 15.37 | Warning | 18 | Warning | 16.24 | Warning | 17.5 | Warning
2 |  |  |  |  | 13.1 | Pass | 11.2 |  | Pass | 10 | Pass | 13.9 | Pass | 10.2 | Pass | 11.29 | Pass | 15.5 | Warning | 28.29 | Fail | 17.14 | Warning | 11.9 | Pass
3 |  |  |  |  | 12.2 | Pass | 10.2 |  | Pass | 9.6 | Pass | 12.8 | Pass | 9.8 | Pass | 9.96 | Pass | 13.77 | Pass | 21.01 | Fail | 14.53 | Pass | 15.6 | Warning
4 |  |  |  |  | 11.2 | Pass | 10.3 |  | Pass | 10.2 | Pass | 11.3 | Pass | 10.3 | Pass | 10.48 | Pass | 14.99 | Pass | 16.08 | Warning | 16.5 | Warning | 18 | Warning
5 |  |  |  |  | 11.6 | Pass | 11.1 |  | Pass | 9.7 | Pass | 11.8 | Pass | 9.8 | Pass | 10.57 | Pass | 14.3 | Pass | 16.65 | Warning | 16.55 | Warning | 12.8 | Pass
6 |  |  |  |  | 12.9 | Pass | 10 |  | Pass | 12.5 | Pass | 12.9 | Pass | 11.7 | Pass | 11.08 | Pass | 19.23 | Warning | 15.97 | Warning | 21.29 | Fail | 23.9 | Fail
7 |  |  |  |  | 11.2 | Pass | 11.9 |  | Pass | 13.7 | Pass | 11.4 | Pass | 12.5 | Pass | 12.66 | Pass | 26.58 | Fail | 16.87 | Warning | 28.84 | Fail | 39.7 | Fail
8 |  |  |  |  | 12 | Pass | 9.6 |  | Pass | 11.9 | Pass | 12.2 | Pass | 10.6 | Pass | 11.98 | Pass | 16.99 | Warning | 16.5 | Warning | 18.38 | Warning | 14.6 | Pass
9 |  |  |  |  | 11.6 | Pass | 12.1 |  | Pass | 10.5 | Pass | 11 | Pass | 9.7 | Pass | 10.11 | Pass | 13.23 | Pass | 15.02 | Warning | 14.85 | Pass | 15.9 | Warning
10 |  |  |  |  | 11.4 | Pass | 11.4 |  | Pass | 9.6 | Pass | 9.8 | Pass | 10.6 | Pass | 9.72 | Pass | 11.7 | Pass | 14.4 | Pass | 13.69 | Pass | 16 | Warning
11 |  |  |  |  | 10.9 | Pass | 10.6 |  | Pass | 10.7 | Pass | 9.5 | Pass | 11.8 | Pass | 10.95 | Pass | 17.56 | Warning | 13.9 | Pass | 13.5 | Pass | 13.5 | Pass
12 |  |  |  |  | 11 | Pass | 11.5 |  | Pass | 10.4 | Pass | 9.8 | Pass | 11.8 | Pass | 11.17 | Pass | 14.96 | Pass | 13.81 | Pass | 13.15 | Pass | 14 | Pass
13 |  |  |  |  | 12.4 | Pass | 11.1 |  | Pass | 9.7 | Pass | 12.1 | Pass | 10.2 | Pass | 10.61 | Pass | 13.08 | Pass | 14.56 | Pass | 15.77 | Warning | 17.8 | Warning
14 |  |  |  |  | 12.2 | Pass | 10.3 |  | Pass | 9.4 | Pass | 12.5 | Pass | 9.9 | Pass | 9.98 | Pass | 12.12 | Pass | 16.85 | Warning | 18.47 | Warning | 19.3 | Warning
15 |  |  |  |  | 11.4 | Pass | 9.9 |  | Pass | 9.5 | Pass | 11.3 | Pass | 10.4 | Pass | 10.58 | Pass | 12.83 | Pass | 12.05 | Pass | 12.47 | Pass | 16.9 | Warning
16 |  |  |  |  | 10.9 | Pass | 10.8 |  | Pass | 11.5 | Pass | 9.5 | Pass | 10.2 | Pass | 12.61 | Pass | 13.02 | Pass | 12.53 | Pass | 13.34 | Pass | 15 | Pass
17 |  |  |  |  | 12.8 | Pass | 11.9 |  | Pass | 10.6 | Pass | 10.7 | Pass | 9.9 | Pass | 9.62 | Pass | 10.37 | Pass | 16.2 | Warning | 10.53 | Pass | 12.5 | Pass
18 |  |  |  |  | 12.1 | Pass | 8.7 |  | Pass | 10.2 | Pass | 10.9 | Pass | 10.5 | Pass | 10.67 | Pass | 16.94 | Warning | 13.15 | Pass | 17.3 | Warning | 13.6 | Pass
19 |  |  |  |  | 12.8 | Pass | 9.9 |  | Pass | 10.9 | Pass | 11.5 | Pass | 10.6 | Pass | 11.19 | Pass | 13.38 | Pass | 14.72 | Pass | 14.33 | Pass | 13.3 | Pass
20 |  |  |  |  | 11.6 | Pass | 9.7 |  | Pass | 10.6 | Pass | 10.6 | Pass | 11.4 | Pass | 10.34 | Pass | 14.86 | Pass | 15.46 | Warning | 16.08 | Warning | 11.8 | Pass
21 |  |  |  |  | 11.8 | Pass | 9.3 |  | Pass | 10.7 | Pass | 10.8 | Pass | 10.2 | Pass | 10.47 | Pass | 15.16 | Warning | 14.61 | Pass | 15.85 | Warning | 13 | Pass
22 |  |  |  |  | 11.6 | Pass | 10 |  | Pass | 11.1 | Pass | 10.8 | Pass | 11.5 | Pass | 12.11 | Pass | 14.69 | Pass | 13.75 | Pass | 14.89 | Pass | 11.8 | Pass
23 |  |  |  |  | 10.7 | Pass | 9.5 |  | Pass | 10.3 | Pass | 10.3 | Pass | 10.5 | Pass | 10.34 | Pass | 12.32 | Pass | 17.21 | Warning | 13.07 | Pass | 12.5 | Pass
24 |  |  |  |  | 9.8 | Pass | 10.2 |  | Pass | 12.9 | Pass | 9.6 | Pass | 11.1 | Pass | 13.19 | Pass | 14.03 | Pass | 10.01 | Pass | 15.29 | Warning | 10.9 | Pass
25 |  |  |  |  | 10.3 | Pass | 9.6 |  | Pass | 10.5 | Pass | 10.3 | Pass | 10 | Pass | 10.79 | Pass | 13.56 | Pass | 12.2 | Pass | 12.4 | Pass | 15.2 | Warning
26 |  |  |  |  | 9.8 | Pass | 9.3 |  | Pass | 9.1 | Pass | 10.3 | Pass | 9.1 | Pass | 9.33 | Pass | 11.97 | Pass | 12.68 | Pass | 14.3 | Pass | 11.5 | Pass
27 |  |  |  |  | 11.1 | Pass | 9.9 |  | Pass | 11.6 | Pass | 11 | Pass | 11.8 | Pass | 11.64 | Pass | 12 | Pass | 14.7 | Pass | 12.62 | Pass | 13 | Pass
28 |  |  |  |  | 10.8 | Pass | 9.1 |  | Pass | 9.8 | Pass | 9.5 | Pass | 9.2 | Pass | 9.65 | Pass | 12.31 | Pass | 13.22 | Pass | 14.93 | Pass | 11.4 | Pass
29 |  |  |  |  | 9.9 | Pass | 9.4 |  | Pass | 11.2 | Pass | 12.9 | Pass | 11 | Pass | 9.72 | Pass | 13.45 | Pass | 12.34 | Pass | 12.11 | Pass | 13 | Pass
30 |  |  |  |  | 12.2 | Pass | 9.8 |  | Pass | 10.4 | Pass | 11 | Pass | 10.5 | Pass | 10.7 | Pass | 13.33 | Pass | 13.81 | Pass | 11.92 | Pass | 11.9 | Pass
31 |  |  |  |  | 10.6 | Pass | 9.6 |  | Pass | 10.8 | Pass | 11.3 | Pass | 9.7 | Pass | 10.32 | Pass | 12.93 | Pass | 11.27 | Pass | 12.03 | Pass | 12.3 | Pass
32 |  |  |  |  | 10.4 | Pass | 10 |  | Pass | 11.3 | Pass | 10.9 | Pass | 9.8 | Pass | 10.87 | Pass | 10.77 | Pass | 13.79 | Pass | 12.8 | Pass | 15.8 | Warning
MCL UPS 2 15 KVA
Battery Spec: | 12 Volts 26 AH
Brand: | Exide Power-Safe
Sr. No. | 2019-01-03 | Comments - 1/3/2019 | 29/3/2019 | Comments - 29/3/2019 | 27/6/2019 | Comments - 27/6/2019 | 19/8/2019 |  | Comments - 19/8/2019 | 27/9/2019 | Comments - 27/9/2019 | 31/10/2019 | Comments - 31/10/2019 | 2019-02-12 | Comments - 2/12/2019 | 2020-09-01 | Comments - 9/1/2020 | 2020-08-12 | Comments - 8/12/2020 | 28/1/2021 | Comments - 28/1/2021 | 2021-09-03 | Comments - 9/3/2021 | 27/4/2021 | Comments - 27/4/2021
1 |  |  |  |  | 12.1 | Pass | 5.7 |  | Pass | 12.2 | Pass | 10 | Pass | 12.5 | Pass | 12.17 | Pass | 16.57 | Warning | 18.53 | Warning | 12.47 | Pass | 16.4 | Warning
2 |  |  |  |  | 13.1 | Pass | 5.8 |  | Pass | 10.1 | Pass | 23.8 | Warning | 18.3 | Warning | 19.24 | Warning | 15.66 | Warning | 16.01 | Warning | 11.33 | Pass | 18.4 | Warning
3 |  |  |  |  | 12.2 | Pass | 5.7 |  | Pass | 10.3 | Pass | 12.1 | Pass | 11.4 | Pass | 12.39 | Pass | 12.41 | Pass | 12.59 | Pass | 12.09 | Pass | 16.7 | Warning
4 |  |  |  |  | 11.2 | Pass | 4.9 |  | Pass | 10 | Pass | 9.6 | Pass | 8.8 | Pass | 11.66 | Pass | 17.07 | Warning | 17.75 | Warning | 13.6 | Pass | 18 | Warning
5 |  |  |  |  | 11.6 | Pass | 5.9 |  | Pass | 10 | Pass | 11.9 | Pass | 10.2 | Pass | 11.18 | Pass | 14.36 | Pass | 14.24 | Pass | 12.05 | Pass | 17.4 | Warning
6 |  |  |  |  | 12.9 | Pass | 6.5 |  | Pass | 11 | Pass | 10.5 | Pass | 10.4 | Pass | 11.25 | Pass | 22.78 | Fail | 24.08 | Fail | 10.37 | Pass | 22.6 | Fail
7 |  |  |  |  | 11.2 | Pass | 9999 |  | Fail | 9.5 | Pass | 10.8 | Pass | 9.5 | Pass | 10.43 | Pass | 22.47 | Fail | 22.88 | Fail | 15.25 | Warning | 31.7 | Fail
8 |  |  |  |  | 12 | Pass | 7.5 |  | Pass | 9.6 | Pass | 11.1 | Pass | 10.5 | Pass | 10.81 | Pass | 12.52 | Pass | 12.94 | Pass | 14.59 | Pass | 19.1 | Warning
9 |  |  |  |  | 11.6 | Pass | 6.4 |  | Pass | 12.3 | Pass | 11.9 | Pass | 11.4 | Pass | 12.64 | Pass | 15.49 | Warning | 14.98 | Pass | 11.44 | Pass | 14.8 | Pass
10 |  |  |  |  | 11.4 | Pass | 5.1 |  | Pass | 12.4 | Pass | 10.7 | Pass | 9.9 | Pass | 13.78 | Pass | 14.54 | Pass | 14.53 | Pass | 12.57 | Pass | 14.3 | Pass
11 |  |  |  |  | 10.9 | Pass | 6.2 |  | Pass | 11.9 | Pass | 15.7 | Warning | 10.9 | Pass | 10.66 | Pass | 15.89 | Warning | 16.12 | Warning | 12.74 | Pass | 20.1 | Fail
12 |  |  |  |  | 11 | Pass | 6.1 |  | Pass | 11.6 | Pass | 11.9 | Pass | 12.3 | Pass | 12.46 | Pass | 16.41 | Warning | 16.91 | Warning | 11.29 | Pass | 17.3 | Warning
13 |  |  |  |  | 12.4 | Pass | 6.4 |  | Pass | 11.8 | Pass | 11.9 | Pass | 10.5 | Pass | 11.9 | Pass | 14.77 | Pass | 15.03 | Warning | 13.29 | Pass | 13.7 | Pass
14 |  |  |  |  | 12.2 | Pass | 6.9 |  | Pass | 10.6 | Pass | 10.6 | Pass | 10 | Pass | 11.53 | Pass | 16.53 | Warning | 17.1 | Warning | 11.97 | Pass | 13.7 | Pass
15 |  |  |  |  | 11.4 | Pass | 5.9 |  | Pass | 9.7 | Pass | 10.8 | Pass | 10.7 | Pass | 10.05 | Pass | 19.44 | Warning | 20.05 | Fail | 13.03 | Pass | 14.7 | Pass
16 |  |  |  |  | 10.9 | Pass |  |  |  | 10.5 | Pass | 11.6 | Pass | 10.3 | Pass | 11.08 | Pass | 16.66 | Warning | 18.36 | Warning | 11.49 | Pass | 12.9 | Pass
17 |  |  |  |  | 12.8 | Pass |  |  |  | 9.6 | Pass | 10.3 | Pass | 9.8 | Pass | 9.56 | Pass | 11.57 | Pass | 11.18 | Pass | 19.32 | Warning | 17 | Warning
18 |  |  |  |  | 12.1 | Pass |  |  |  | 9.8 | Pass | 10.5 | Pass | 9.5 | Pass | 9.7 | Pass | 13.57 | Pass | 13.66 | Pass | 15.64 | Warning | 16.1 | Warning
19 |  |  |  |  | 12.8 | Pass |  |  |  | 9.9 | Pass | 10.4 | Pass | 10 | Pass | 9.66 | Pass | 13.61 | Pass | 13.68 | Pass | 21.9 | Fail | 14.5 | Pass
20 |  |  |  |  | 11.6 | Pass |  |  |  | 9.1 | Pass | 10.9 | Pass | 9.2 | Pass | 8.95 | Pass | 12.29 | Pass | 13.4 | Pass | 13.75 | Pass | 14.7 | Pass
21 |  |  |  |  | 11.8 | Pass |  |  |  | 9.4 | Pass | 10.6 | Pass | 9.5 | Pass | 10.34 | Pass | 11.46 | Pass | 11.6 | Pass | 17.04 | Warning | 18 | Warning
22 |  |  |  |  | 11.6 | Pass |  |  |  | 9.1 | Pass | 11.6 | Pass | 9.7 | Pass | 11.64 | Pass | 12.03 | Pass | 12.57 | Pass | 15.05 | Warning | 12.9 | Pass
23 |  |  |  |  | 10.7 | Pass |  |  |  | 9.3 | Pass | 11.7 | Pass | 9.4 | Pass | 10.62 | Pass | 11.46 | Pass | 11.73 | Pass | 15.96 | Warning | 10.9 | Pass
24 |  |  |  |  | 9.8 | Pass |  |  |  | 8.8 | Pass | 11.2 | Pass | 9.5 | Pass | 9.29 | Pass | 12.76 | Pass | 13.03 | Pass | 16.12 | Warning | 17.1 | Warning
25 |  |  |  |  | 10.3 | Pass |  |  |  | 11.1 | Pass | 11.6 | Pass | 10.5 | Pass | 10.42 | Pass | 12.18 | Pass | 11.45 | Pass | 18.02 | Warning | 13.6 | Pass
26 |  |  |  |  | 9.8 | Pass |  |  |  | 8.7 | Pass | 11.1 | Pass | 9.9 | Pass | 9.66 | Pass | 13.14 | Pass | 13.42 | Pass | 13.39 | Pass | 13.2 | Pass
27 |  |  |  |  | 11.1 | Pass |  |  |  | 9.8 | Pass | 10.5 | Pass | 9.8 | Pass | 9.81 | Pass | 9.59 | Pass | 9.65 | Pass | 15.8 | Warning | 13.2 | Pass
28 |  |  |  |  | 10.8 | Pass |  |  |  | 9.5 | Pass | 11.1 | Pass | 10.8 | Pass | 11.07 | Pass | 9.61 | Pass | 13.89 | Pass | 22.39 | Fail | 13.9 | Pass
29 |  |  |  |  | 9.9 | Pass |  |  |  | 9.8 | Pass | 11 | Pass | 11.4 | Pass | 12.51 | Pass | 14.3 | Pass | 15.2 | Pass | 11.07 | Pass | 14.7 | Pass
30 |  |  |  |  | 12.2 | Pass |  |  |  | 10.7 | Pass | 11.4 | Pass | 8.8 | Pass | 9.55 | Pass | 15.03 | Warning | 12.75 | Pass | 9999 | Fail | 14.3 | Pass
31 |  |  |  |  | 10.6 | Pass |  |  |  | 9.6 | Pass | 9.8 | Pass | 10.6 | Pass | 10.48 | Pass | 11.77 | Pass | 12.57 | Pass | 16.51 | Warning | 11.9 | Pass
32 |  |  |  |  | 10.4 | Pass |  |  |  | 10.1 | Pass | 12.8 | Pass | 9.6 | Pass | 9.96 | Pass | 12.68 | Pass | 13.25 | Pass | 13.9 | Pass | 12.2 | Pass
[18 empty] | 12.6 | Pass
IT Team Office 5 KVA UPS
Battery Spec:
Brand:
Sr. No. | 2019-01-03 | Comments - 1/3/2019 | 29/3/2019 | Comments - 29/3/2019 | 27/6/2019 | Comments - 27/6/2019 |  |  |  | 27/9/2019 | Comments - 27/9/2019 | 31/10/2019 | Comments - 31/10/2019 | 27/1/2021 | Comments - 27/1/2021 | 2020-03-02 |  | 2021-09-03 | Comments - 9/3/2021
1 | [13 empty] | 5.51 | Pass |  |  | 4.6 | Pass
2 | [13 empty] | 9.49 | Pass |  |  | 4.6 | Pass
3 | [13 empty] | 4.79 | Pass |  |  | 5 | Pass
4 | [13 empty] | 7.7 | Pass |  |  | 6.4 | Pass
5 | [13 empty] | 6.61 | Pass |  |  | 4.7 | Pass
6 | [13 empty] | 7.93 | Pass |  |  | 6.3 | Pass
7 | [13 empty] | 12.66 | Warning | Changed |  | 6 | Pass
8 | [13 empty] | 11.93 | Warning | Changed |  | 6.8 | Pass
9 | [13 empty] | 9999 | Fail | Changed |  | 3.9 | Pass
10 | [13 empty] | 9999 | Fail | Changed |  | 4.2 | Pass
11 | [13 empty] | 4.77 | Pass |  |  | 4 | Pass
12 | [13 empty] | 5.66 | Pass |  |  | 5 | Pass
13 | [13 empty] | 5.47 | Pass |  |  | 4.7 | Pass
14
15
16
Micro 2 Lab XPS 10 KVA UPS
Battery Spec: | 12 Volts 65 AH
Brand: | Amara Raja QUANTA
Sr. No. | 2019-01-03 | Comments - 1/3/2019 | 29/3/2019 | Comments - 29/3/2019 | 27/6/2019 | Comments - 27/6/2019 |  | 19/8/2019 | Comments - 19/8/2019 | 27/9/2019 | Comments - 27/9/2019 | 31/10/2019 | Comments - 31/10/2019 | 29/11/2019 | Comments - 29/11/2019 | 2020-08-12 | Comments - 8/12/2020 | 2021-01-02 | 17/2/2021 | Comments - 17/2/2021 |  | 27/4/2021 | Comments - 27/4/2021
1 |  |  | 8.3 | Pass | 10.3 | Pass |  | 12 | Warning | 12.1 | Warning | 9.7 | Pass | 9.8 | Pass | 14.92 | Warning | Changed |  | Reading got missed |  | 5.9 | Pass
2 |  |  | 8.8 | Pass | 9.4 | Pass |  | 11.1 | Pass | 9.2 | Pass | 10.3 | Pss | 10.5 | Pass | 15.86 | Warning | Changed | 6.12 | Pass |  | 5.9 | Pass
3 |  |  | 12.8 | Warning | 20.6 | Fail |  | 10.1 | Pass | 21 | Fail | 22.7 | Fail | 22.3 | Fail | 19.23 | Fail | Changed | 6.14 | Pass |  | 6.2 | Pass
4 |  |  | 8.1 | Pass | 8.8 | Pass |  | 10 | Pass | 9.7 | Pass | 9.4 | Pass | 9.7 | Pass | 14.31 | Warning | Changed | 6.23 | Pass |  | 6.9 | Pass
5 |  |  | 10 | Pass | 11.3 | Pass |  | 9.8 | Pass | 9.2 | Pass | 12.6 | Warning | 12.9 | Warning | 18.02 | Fail | Changed | 6.21 | Pass |  | 6.4 | Pass
6 |  |  | 10.5 | Pass | 12.1 | Warning |  | 10.6 | Pass | 11.2 | Pass | 11.7 | Pass | 12 | Warning | 14.7 | Warning | Changed | 6.39 | Pass |  | 6 | Pass
7 |  |  | 11.4 | Pass | 9.3 | Pass |  | 12.9 | Warning | 13.6 | Warning | 9.7 | Pass | 10 | Pass | 12.86 | Warning | Changed | 6.38 | Pass |  | 6 | Pass
8 |  |  | 8.8 | Pass | 9.3 | Pass |  | 11.9 | Pass | 9.5 | Pass | 9.9 | Pass | 10.1 | Pass | 14.3 | Warning | Changed | 6.36 | Pass |  | 5.7 | Pass
9 |  |  | 8.7 | Pass | 13.5 | Warning |  | 11 | Pass | 9.4 | Pass | 14.8 | Warning | 15.6 | Warning | 18.1 | Fail | Changed | 6.24 | Pass |  | 6.4 | Pass
10 |  |  | 9.8 | Pass | 11.2 | Pass |  | 11.1 | Pass | 11.3 | Pass | 12 | Warning | 12.3 | Warning | 16.64 | Fail | Changed | 6.15 | Pass |  | 6.7 | Pass
11 |  |  | 10.4 | Pass | 12.5 | Warning |  | 9.4 | Pass | 12.9 | Warning | 12.7 | Warning | 13 | Warning | 15.97 | Warning | Changed | 6.11 | Pass |  | 6.6 | Pass
12 |  |  | 10.2 | Pass | 11.9 | Pass |  | 10.4 | Pass | 11.4 | Pass | 11.5 | Pass | 11.9 | Pass | 14.35 | Warning | Changed | 6.03 | Pass |  | 6.9 | Pass
13 |  |  | 13.5 | Warning | 15.7 | Warning |  | 10.5 | Pass | 16 | Pass | 18 | Fail | 17.7 | Fail | 18.59 | Fail | Changed | 6.12 | Pass |  | 6 | Pass
14 |  |  | 9.8 | Pass | 11 | Pass |  | 10.6 | Pass | 10.9 | Pass | 11.9 | Pass | 12.1 | Warning | 13.84 | Warning | Changed | 6.17 | Pass |  | 6.2 | Pass
15 |  |  | 9.5 | Pass | 12.4 | Warning |  | 9.7 | Pass | 11.4 | Pass | 13.7 | Warning | 14.6 | Warning | 19.9 | Fail | Changed | 6.14 | Pass |  | 7.2 | Pass
16 |  |  | 8.7 | Pass | 9.3 | Pass |  | 9.6 | Pass | 9.8 | Pass | 10.4 | Pass | 10.7 | Pass | 14.6 | Warning | Changed | 6.24 | Pass |  | 5.9 | Pass
17 |  |  | 8.8 | Pass | 9.7 | Pass |  | 9.8 | Pass | 9.2 | Pass | 10.2 | Pass | 10.5 | Pass | 16.57 | Fail | Changed | 6.29 | Pass |  | 5.6 | Pass
18 |  |  | 8.9 | Pass | 9.9 | Pass |  | 11.6 | Pass | 9.4 | Pass | 10 | Pass | 11.2 | Pass | 13.59 | Warning | Changed | 6.06 | Pass |  | 5.8 | Pass
19 |  |  | 8.8 | Pass | 10.3 | Pass |  | 10.8 | Pass | 9.7 | Pass | 9.8 | Pass | 9.9 | Pass | 13.9 | Warning | Changed | 6.14 | Pass |  | 6.1 | Pass
20 |  |  | 8.8 | Pass | 9.8 | Pass |  | 10.7 | Pass | 9.8 | Pass | 10.5 | Pass | 10.6 | Pass | 14.27 | Warning | Changed | 6.26 | Pass |  | 5.9 | Pass
9.9
11.1
10.6
12.8
10.4
9.9
10.5
9.5
9.5
12.2
9.1
11.3
HSC [OE] [NCPRE] Lab UPS - Newly Added
Battery Spec:
Brand:
Sr. No. | 31/10/2019 | Comments - 31/10/2019 | 29/11/2019 | Comments - 29/11/2019 | 2020-09-01 | Comments - 9/1/2020
1 | 13.6 |  | 13.2 |  | 12.86
2 | 13.8 |  | 13.4 |  | 12.66
3 | 13.2 |  | 13.4 |  | 12.27
4 | 14.2 |  | 14.7 |  | 12.87
5 | 12.9 |  | 12.8 |  | 12.32
6 | 12.5 |  | 12.5 |  | 13.18
7 | 13.5 |  | 13.5 |  | 13.05
8 | 13.5 |  | 13.5 |  | 12.76
9 | 13.7 |  | 14.3 |  | 12.41
10 | 12.3 |  | 13.6 |  | 12.77
11 | 13.2 |  | 13.9 |  | 12.63
12 | 12.6 |  | 13.7 |  | 12.29
13 | 12 |  | 13.3 |  | 12.05
14 | 12.5 |  | 12.8 |  | 12.52
15 | 11.4 |  | 11.5 |  | 11.65
16 | 13.5 |  | 12.2 |  | 12.57
17 | 12 |  | 12.7 |  | 12.59
18 | 11.9 |  | 12.5 |  | 12.13
19 | 11.9 |  | 12.6 |  | 12.09
20 | 12.1 |  | 12.5 |  | 12.5
21 | 12.3 |  | 12.8 |  | 12.39
22 | 11.8 |  | 12.4 |  | 11.87
23 | 12 |  | 12.5 |  | 12.22
24 | 12.5 |  | 12.8 |  | 13.26
25 | 12.6 |  | 12.7 |  | 12.67
26 | 12 |  | 12.7 |  | 12.24
27 | 12.1 |  | 12.5 |  | 13.77
28 | 12.1 |  | 12.5 |  | 12.56
29 | 12.1 |  | 12.8 |  | 12.57
30 | 12.8 |  | 13.2 |  | 13.17
31 | 12.7 |  | 12.4 |  | 12.95
32 | 14.3 |  | 14.1 |  | 14.62
33 | 11.6 |  | 12.5 |  | 12.1
34 | 13.1 |  | 13.3 |  | 12.72
35 | 13.1 |  | 13.1 |  | 12.58
36 | 11.5 |  | 12.1 |  | 11.53
37 | 12.3 |  | 12.7 |  | 12.3
38 | 12.6 |  | 12.8 |  | 12.45
39 | 11.9 |  | 12 |  | 11.85
40 | 12.7 |  | 13.5 |  | 12.79